## Temp Calc (hidden)
CABLING DETAILS |  |  | POWER OVER ETHERNET
 Equipment cord (Floor Distributor side) |  |  | Power @ PD | 71.3 | 4
Wire gauge | AWG24/7 |  | Vpse | 50
Category and construction | Cat.6 UTP |  | Conductors | 8
Length | 2
Patch cord reference | ACTPC6ASFLS20yy (yy = color code)
EL-number |  |  | CABLE PATHWAY
Bundle size
Ambient temperature | 20
Note: bundle of patch cords are supposed to be in ventilated envrionment
 Horizontal cable |  |  | ROUND BUNDLE CALCULATION
Category |  |  | Worst case channel IL
Construction |  |  | Average power loss
CPR Euroclass |  |  | Power efficiency (vs PPSE)
Patch cord reference |  |  | Average Consumption / 24h
EL-number
|  |  | Central equipment cord ΔT | [14 empty] | CABLE 2
Length
Bundle size |  |  | Central horizontal cable ΔT | [36 empty] | 191 |  | 179 |  | 165 |  | 178 |  | 190 | [10 empty] | 49.4299
Installation environment | [36 empty] | 172 |  | 155 |  | 143 |  | 131 |  | 130 |  | 142 |  | 154 |  | 171 | [7 empty] | 48.6653
Ambient temperature | 25 | [32 empty] | 192 |  | 156 |  | 109 |  | 108 |  | 107 |  | 106 |  | 105 |  | 104 |  | 103 |  | 153 |  | 189 |  |  |  |  | 47.9008
Installation environment | [16 empty] | 39.4299 | [15 empty] | 180 |  | 144 |  | 110 |  | 76 |  | 75 |  | 74 |  | 73 |  | 72 |  | 71 |  | 102 |  | 141 |  | 177 |  |  |  | 47.1363
[32 empty] | 166 |  | 132 |  | 111 |  | 77 |  | 49 |  | 48 |  | 47 |  | 46 |  | 45 |  | 70 |  | 101 |  | 129 |  | 164 |  |  | 46.3717
 Work area cord (End user side) | [30 empty] | 181 |  | 133 |  | 112 |  | 78 |  | 50 |  | 28 |  | 27 |  | 26 |  | 25 |  | 44 |  | 69 |  | 100 |  | 128 |  | 176 |  | 45.6072
Wire gauge | AWG24/7 | [6 empty] | 37.7377 |  | 37.7377 |  | 37.7377 |  | 37.1973 | [6 empty] | 48.0921 |  | 48.0921 |  | 48.0921 |  | 46.3085 |  |  | 193 |  | 145 |  | 113 |  | 79 |  | 51 |  | 29 |  | 13 |  | 12 |  | 11 |  | 24 |  | 43 |  | 68 |  | 99 |  | 140 |  | 188 | 44.8427
Category and construction | Cat.6 UTP | [5 empty] | 37.6026 |  | 38.0078 |  | 38.0078 |  | 37.7377 |  | 37.1973 |  |  |  |  | 47.6462 |  | 48.984 |  | 48.984 |  | 48.0921 |  | 46.3085 |  |  | 157 |  | 114 |  | 80 |  | 52 |  | 30 |  | 14 |  | 4 |  | 3 |  | 10 |  | 23 |  | 42 |  | 67 |  | 98 |  | 152 |  | 44.0781
Length | 2 |  |  |  |  | 37.6026 |  | 38.0078 |  | 38.1429 |  | 38.0078 |  | 37.7377 |  | 37.1973 |  |  | 47.6462 |  | 48.984 |  | 49.4299 |  | 48.984 |  | 48.0921 |  | 46.3085 | 173 |  | 115 |  | 81 |  | 53 |  | 31 |  | 15 |  | 5 |  | 1 |  | 2 |  | 9 |  | 22 |  | 41 |  | 66 |  | 97 |  | 170 | 43.3136
Patch cord reference | ACTPC6ASFLS20yy (yy = color code) | [5 empty] | 37.6026 |  | 38.0078 |  | 38.0078 |  | 37.7377 |  | 37.1973 |  |  |  |  | 47.6462 |  | 48.984 |  | 48.984 |  | 48.0921 |  | 46.3085 |  |  | 158 |  | 116 |  | 82 |  | 54 |  | 32 |  | 16 |  | 6 |  | 7 |  | 8 |  | 21 |  | 40 |  | 65 |  | 96 |  | 163 |  | 42.5491
EL-number | [7 empty] | 37.6026 |  | 37.6026 |  | 37.6026 |  | 37.1973 | [6 empty] | 47.6462 |  | 47.6462 |  | 47.6462 |  | 46.3085 |  |  | 194 |  | 146 |  | 117 |  | 83 |  | 55 |  | 33 |  | 17 |  | 18 |  | 19 |  | 20 |  | 39 |  | 64 |  | 95 |  | 151 |  | 199 | 41.7845
[31 empty] | 182 |  | 134 |  | 118 |  | 84 |  | 56 |  | 34 |  | 35 |  | 36 |  | 37 |  | 38 |  | 63 |  | 94 |  | 139 |  | 187 |  | 41.02
Ambient temperature | 25 | [30 empty] | 167 |  | 135 |  | 119 |  | 85 |  | 57 |  | 58 |  | 59 |  | 60 |  | 61 |  | 62 |  | 93 |  | 138 |  | 169 |  |  | 40.2555
[33 empty] | 183 |  | 147 |  | 120 |  | 86 |  | 87 |  | 88 |  | 89 |  | 90 |  | 91 |  | 92 |  | 150 |  | 186 |  |  |  | 39.4909
[34 empty] | 195 |  | 159 |  | 121 |  | 122 |  | 123 |  | 124 |  | 125 |  | 126 |  | 127 |  | 162 |  | 198 |  |  |  |  | 38.7264
[37 empty] | 174 |  | 160 |  | 148 |  | 136 |  | 137 |  | 149 |  | 161 |  | 175 | [7 empty] | 37.9619
[40 empty] | 196 |  | 184 |  | 168 |  | 185 |  | 197 | [10 empty] | 37.1973
Calculation 1 | round bundle
Calculation 2 | in cable pathway
Calculation 3 | bundles of 24 with separation distance
Ambient temp | 35
Horizontal cable length
in bundle (L1) | 7 | → L1+L2 shall be greater than 10m
@20°C (L2) | 0
S patch cord length (20°C) | 60 | → shall be between 1 and 10m
Number of connections | 2
| CABLE 1 | CABLE 2
Cable ref | VDICD116--- | Patch AWG28 U
Cable description | Cat.6 U/UTP | Cat.6 U/UTP
Bundle size | 12 | 12
Installation environment | Under ventilated conditions | Under ventilated conditions
For central cable :
Δ temp | 3.1429 | 14.4299
Cable temp | 38.1429 | 49.4299
Perm. Link IL | 8.342% | 8.84%
Average cable loss | 8.7689 | 10.6539
Power efficiency (vs PPSE) | 89.05% | 87%
Cable factor | 5 | 5
Cable diameter | 5.9 | 3.8
Environment factor | 0.15 | 0.15
R(20°C) | 0.51678 | 1.5599
R(ambient) | 0.54701 | 1.6512
Rcable(ambient) | 0.2735 | 0.82558
Rpatch(20°C) | 3.3221 | 3.3221
Rcable(20°C) | 0 | 0
Rconnections | 0.1 | 0.1
Icable(ambient) | 1.62 | 1.6601
IL(°C) coeff < 40°C | 0.4% | 0.4%
IL(°C) coeff > 40°C | 0.6% | 0.6%

## Cable list (hidden)
Cable reference |  |  | Category | Construction | Supplier | Copper diameter | Insulation | NVP | Overal diameter (mm) | Fire load (MJ/km) | Cable weight (kg/km) | Avg twist step | Avg resistance per conductor (ohm/km) | IL(°C) coeff < 40°C | IL(°C) coeff > 40°C | Construction (for heating consideration) | Cable constant | Theoretical copper content | Copper content (kg/km) | Drain wire | Copper wire content | E-number Denmark | E-number Finland | E-number Norway | E-number Sweden
VDICD115218 | 1 | VDICD115218 | Cat.5e | U/UTP | Nexans | 0.505 | 0.89 | 68 | 4.9 | 391 | 30.9 | 14 | 86.5504 | 0.4 | 0.6 | U/UTP | 5 | 14.5754 | 14.6 |  | 14.6
VDICD135218 | 1 | VDICD135218 | Cat.5e | F/UTP | Nexans | 0.51 | 1.06 | 68 | 6 | 513 | 41.2 | 14 | 85.5401 | 0.2 | 0.2 | F/UTP | 3 | 14.9843 | 16.6 | 1.1209 | 15.4791
VDICD116218 | 1 | VDICD116218 | Cat.6 | U/UTP | Nexans | 0.55 | 0.97 | 68 | 5.9 | 599 | 40.9 | 12 | 73.8251 | 0.4 | 0.6 | U/UTP | 5 | 17.492 | 18.2 |  | 18.2
VDICC116118 | 1 | VDICC116118 | Cat.6 | U/UTP | Prysmian | 0.565 | 1 | 67 | 5.9 | 504 | 44 | 12 | 70.0902 | 0.4 | 0.6 | U/UTP | 5 | 18.4943 | 17.991
VDICD116018WHD | 1 | VDICD116018WHD | Cat.6 | U/UTP | Prysmian | 0.54 | 0.95 | 67 | 5.4 | 316 | 36 | 100 | 74.2617 | 0.4 | 0.6 | U/UTP | 5 | 16.3503 | 16.36
VDICD116118GHD | 0 |  | Cat.6 | U/UTP | Prysmian | 0.54 | 0.95 | 66 | 5.4 | 316 | 36 | 12 | 76.49 | 0.4 | 0.6 | U/UTP | 5 | 16.8409 | 16.36
VDICD116118GHD | 1 | VDICD116118GHD | Cat.6 | U/UTP | Nexans | 0.54 | 0.95 | 66 | 5.5 |  | 35 | 12 | 76.49 | 0.4 | 0.6 | U/UTP | 5 | 16.8409
VDICD416118 | 1 | VDICD416118 | Cat.6 | U/UTP | Prysmian | 0.54 | 0.95 | 66 | 5.4 | 316 | 36 | 12 | 76.49 | 0.4 | 0.6 | U/UTP | 5 | 16.8409 | 16.36
VDICD136218 | 1 | VDICD136218 | Cat.6 | F/UTP | Nexans | 0.54 | 1.13 | 68 | 7.1 | 821 | 49 | 12 | 77.4087 | 0.2 | 0.2 | F/UTP | 3 | 17.0432 | 18.4 | 1.1209 | 17.2791
VDICD176218 | 1 | VDICD176218 | Cat.6 | SF/UTP | Prysmian | 0.545 | 1.16 | 66 | 7.4 |  |  | 12 | 76.1592 | 0.2 | 0.2 | XTP | 2.8 | 17.3978
VDICD626218 | 1 | VDICD626218 | Cat.6 | U/FTP | Prysmian | 0.55 | 1.38 | 75 | 6.9 | 496 | 48 | 12 | 76.0806 | 0.2 | 0.2 | U/FTP | 2.9 | 18.0265 | 18.485 | 1.1209
VDICD626218 | 0 |  | Cat.6 | U/FTP | Nexans | 0.565 | 1.3 | 80 | 7.1 | 525 | 48 | 12 | 71.6245 | 0.2 | 0.2 | U/FTP | 2.9 | 18.8991
VDICD60X218 | 0 |  | Cat.6A | U/UTP | Prysmian | 0.56 | 1.18 | 66 | 7.55 |  | 60 | 8 | 76.0715 | 0.2 | 0.2 | F/UTP | 3 | 19.3713
VDICD60X218 | 1 | VDICD60X218 | Cat.6A | U/UTP | Prysmian | 0.565 | 1.18 | 66 | 7.7 | 585 | 60 | 8 | 74.7311 | 0.2 | 0.2 | F/UTP | 3 | 19.7188
VDICD13X218 | 1 | VDICD13X218 | Cat.6A | F/UTP | Nexans | 0.565 | 1.18 | 68 | 7.5 | 861 | 50 | 8 | 74.7311 | 0.2 | 0.2 | F/UTP | 3 | 19.7188
VDICD63X218 | 1 | VDICD63X218 | Cat.6A | F/UTP | Nexans | 0.565 | 1.18 | 68 | 7.5 | 861 | 50 | 8 | 74.7311 | 0.2 | 0.2 | F/UTP | 3 | 19.7188
VDICD62X218 | 1 | VDICD62X218 | Cat.6A | U/FTP | Prysmian | 0.56 | 1.38 | 76 | 7.7 |  |  | 12 | 73.3877 | 0.2 | 0.2 | U/FTP | 2.9 | 18.6879
VDICD62X218 | 0 |  | Cat.6A | U/FTP | Nexans | 0.565 | 1.3 | 80 | 7.1 | 525 | 48 | 12 | 71.6245 | 0.2 | 0.2 | U/FTP | 2.9 | 18.8991
VDICD64X218 | 0 |  | Cat.6A | F/FTP | Prysmian | 0.56 | 1.38 | 76 | 7.8 |  |  | 12 | 73.3877 | 0.2 | 0.2 | F/FTP | 2.85 | 18.6879
VDICD64X218 | 1 | VDICD64X218 | Cat.6A | F/FTP | Nexans | 0.565 | 1.3 | 82 | 7.5 | 525 | 48 | 12 | 71.6245 | 0.2 | 0.2 | F/FTP | 2.85 | 18.8991
VDICC64X218 | 0 |  | Cat.6A | F/FTP | Prysmian | 0.56 | 1.38 | 76 | 8.2 | 806 | 76 | 12 | 73.3877 | 0.2 | 0.2 | F/FTP | 2.85 | 18.6879
VDICC64X218 | 1 | VDICC64X218 | Cat.6A | F/FTP | Nexans | 0.565 | 1.3 | 80 | 7.8 |  | 51 | 12 | 71.6245 | 0.2 | 0.2 | F/FTP | 2.85 | 18.8991 | 19.84
VDICD68X218 | 1 | VDICD68X218 | Cat.6A | XTP | Nexans | 0.565 | 1.3 | 82 | 7.7 | 595 | 54 | 12 | 71.6245 | 0.2 | 0.2 | XTP | 2.8 | 18.8991
VDICC68X218 | 1 | VDICC68X218 | Cat.6A | XTP | Nexans | 0.565 | 1.3 | 82 | 8.1 | 765 | 63 | 12 | 71.6245 | 0.2 | 0.2 | XTP | 2.8 | 18.8991
VDICD687218 | 1 | VDICD687218 | Cat.7 | XTP | Nexans | 0.565 | 1.3 | 82 | 7.7 | 595 | 54 | 12 | 71.6245 | 0.2 | 0.2 | XTP | 2.8 | 18.8991
VDICD648218 | 0 |  | Cat.7A | F/FTP | Prysmian | 0.58 | 1.4 | 76 | 8 |  |  | 12 | 68.5289 | 0.2 | 0.2 | F/FTP | 2.85 | 20.0804
VDICD648218 | 1 | VDICD648218 | Cat.7A | F/FTP | Nexans | 0.575 | 1.3 | 80 | 7.5 | 597 | 57 | 12 | 69.1548 | 0.2 | 0.2 | F/FTP | 2.85 | 19.574 | 22.1
VDICC648218 | 0 |  | Cat.7A | F/FTP | Prysmian | 0.58 | 1.46 | 76 | 8.4 | 525 | 80 | 12 | 68.8833 | 0.2 | 0.2 | F/FTP | 2.85 | 20.1842
VDICC648218 | 1 | VDICC648218 | Cat.7A | F/FTP | Nexans | 0.575 | 1.3 | 80 | 7.9 |  | 58 | 12 | 69.1548 | 0.2 | 0.2 | F/FTP | 2.85 | 19.574 | 22.1
VDICD658218 | 1 | VDICD658218 | Cat.7A | S/FTP | Nexans | 0.575 | 1.3 | 80 | 7.6 | 566 | 59 | 12 | 69.1548 | 0.2 | 0.2 | S/FTP | 2.75 | 19.574
VDICC658218 | 1 | VDICC658218 | Cat.7A | S/FTP | Nexans | 0.575 | 1.3 | 80 | 8 | 766 | 71 | 12 | 69.1548 | 0.2 | 0.2 | S/FTP | 2.75 | 19.574 | 23.4
ACTTG4P6ASCM3RBU | 1 | ACTTG4P6ASCM3RBU | Cat.6A | F/UTP |  | 0.565 | 1.15 |  | 7.3 |  |  | 8 | 74.3988 | 0.2 | 0.2 | F/UTP | 3 | 19.6311
ACTTG4P6ASLS3RWE | 1 | ACTTG4P6ASLS3RWE | Cat.6A | F/UTP |  | 0.565 | 1.15 |  | 7.3 |  |  | 8 | 74.3988 | 0.2 | 0.2 | F/UTP | 3 | 19.6311
ACT4P6UCM3RBBU | 1 | ACT4P6UCM3RBBU | Cat.6 | U/UTP |  | 0.565 | 1.04 |  | 6 |  |  | 12 | 70.2734 | 0.4 | 0.6 | U/UTP | 5 | 18.5426
ACT4P6ULS3RBWE | 1 | ACT4P6ULS3RBWE | Cat.6 | U/UTP |  | 0.565 | 1.04 |  | 6 |  |  | 12 | 70.2734 | 0.4 | 0.6 | U/UTP | 5 | 18.5426
AWG26/7_Cat.5e UTP | 1 | AWG26/7_Cat.5e UTP |  | U/UTP |  | 0.35 | 0.93 |  | 4.5 |  |  | 8 | 188.1094 | 0.4 | 0.6 | U/UTP | 5 | 7.3092
AWG26/7_Cat.5e FTP | 1 | AWG26/7_Cat.5e FTP |  | F/UTP |  | 0.35 | 0.93 |  | 5.5 |  |  | 8 | 188.1094 | 0.2 | 0.2 | F/UTP | 3 | 7.3092
AWG26/7_Cat.6 UTP | 1 | AWG26/7_Cat.6 UTP |  | U/UTP |  | 0.38 | 0.96 |  | 5 |  |  | 8 | 160.1947 | 0.4 | 0.6 | U/UTP | 5 | 8.649
AWG26/7_Cat.6 FTP | 1 | AWG26/7_Cat.6 FTP |  | F/UTP |  | 0.38 | 0.96 |  | 6 |  |  | 8 | 160.1947 | 0.2 | 0.2 | F/UTP | 3 | 8.649
AWG26/7_Cat.6A UTP | 1 | AWG26/7_Cat.6A UTP |  | S/FTP |  | 0.4 | 0.98 |  | 6 |  |  | 12 | 139.6632 | 0.2 | 0.2 | S/FTP | 2.75 | 9.2578
AWG26/7_Cat.6A STP | 1 | AWG26/7_Cat.6A STP |  | S/FTP |  | 0.4 | 0.98 |  | 6 |  |  | 12 | 139.6632 | 0.2 | 0.2 | S/FTP | 2.75 | 9.2578
AWG28/7_Cat.6 UTP | 1 | AWG28/7_Cat.6 UTP | Cat.6 | U/UTP |  | 0.32 | 0.85 |  | 3.8 |  |  | 8 | 222.8424 | 0.4 | 0.6 | U/UTP | 5 | 6.0504
AWG28/7_Cat.6 FTP | 1 | AWG28/7_Cat.6 FTP | Cat.6 | F/UTP |  | 0.32 | 0.85 |  | 5.2 |  |  | 8 | 222.8424 | 0.2 | 0.2 | F/UTP | 3 | 6.0504
AWG28/7_Cat.6A STP | 1 | AWG28/7_Cat.6A STP | Cat.6A | S/FTP |  | 0.32 | 0.85 |  | 5.5 |  |  | 8 | 222.8424 | 0.2 | 0.2 | S/FTP | 2.75 | 6.0504
VDICD136018 | CAB LAN FUTP 4P CAT6 250 MHZ LSZH 100M
VDICC116218 | CAB LAN UUTP 4P CAT6 250 MHZ LSZH 500M
VDICC62X218 | CAB LAN UFTP 4P CAT6A 550 MHZ LSZH 500M
VDICD687218 | CAB LAN MX FFTP 4P CAT7 LSZH 500M
VDICD687228 | CAB LAN MX FFTP 2X4P CAT7 LSZH 500M
VDICD136028 | CAB LAN FUTP 2x4P CAT6 250 MHZ LSZH 100M
VDICC657218 | CAB LAN SFTP CAT7 Cca 500m
VDICD657218 | CAB LAN SFTP CAT7 Dca 500m
VDICC60X218 | CAB LAN UUTP 4P CAT6a 500 MHZ LSZH 500M
VDICD136018 | CAB LAN FUTP 4P CAT6 250 MHZ LSZH 100M
VDICC116218 | CAB LAN UUTP 4P CAT6 250 MHZ LSZH 500M
VDICC62X218 | CAB LAN UFTP 4P CAT6A 550 MHZ LSZH 500M
VDICD687218 | CAB LAN MX FFTP 4P CAT7 LSZH 500M
VDICD687228 | CAB LAN MX FFTP 2X4P CAT7 LSZH 500M
VDICC657218 | CAB LAN SFTP CAT7 Cca 500m
VDICD657218 | CAB LAN SFTP CAT7 Dca 500m
VDICC60X218 | CAB LAN UUTP 4P CAT6a 500 MHZ LSZH 500M
VDICD136018 | CAB LAN FUTP 4P CAT6 250 MHZ LSZH 100M | NEXANS | FUMAY - FRANCE
VDICC116218 | CAB LAN UUTP 4P CAT6 250 MHZ LSZH 500M | PRYSMIAN | WASHINGTON -UK
VDICC62X218 | CAB LAN UFTP 4P CAT6A 550 MHZ LSZH 500M | PRYSMIAN | NUREMBERG - GERMANY
VDICD687218 | CAB LAN MX FFTP 4P CAT7 LSZH 500M | NEXANS | FUMAY - FRANCE
VDICD687228 | CAB LAN MX FFTP 2X4P CAT7 LSZH 500M | NEXANS | FUMAY - FRANCE
VDICC657218 | CAB LAN SFTP CAT7 Cca 500m | PRYSMIAN | NUREMBERG - GERMANY
VDICD657218 | CAB LAN SFTP CAT7 Dca 500m | PRYSMIAN | NUREMBERG - GERMANY
VDICC60X218 | CAB LAN UUTP 4P CAT6a 500 MHZ LSZH 500M | PRYSMIAN | WASHINGTON -UK
Note on G12: SESA43540: Seb's file : 0.55mm
Note on G13: SESA43540: Seb's file : 0.56mm
Note on J13: SESA43540: Seb's file : 7.7mm
Note on J22: SESA43540: Seb's file : 7mm
Note on J24: SESA43540: Seb's file : 7.4mm
Note on J25: SESA43540: Seb's file : 7.3mm
Note on J26: SESA43540: Seb's file : 7.7mm
Note on J27: SESA43540: Seb's file : 7.3mm
Note on G29: SESA43540: Seb's file : 0.565mm
Note on G31: SESA43540: Seb's file : 0.565mm
Note on G32: SESA43540: Seb's file : 0.565mm
Note on J32: SESA43540: Seb's file : 7.3mm
Note on G33: SESA43540: Seb's file : 0.565mm
Note on J33: SESA43540: Seb's file : 7.9mm

## Constant list (hidden)
ρu is the constant relating to installation environment
Under ventilated conditions |  | 1 | 0.15
In plastic conduits or open metal trays |  | 2 | 0.25
In closed metal trays |  | 3 | 0.5
With insulation |  | 4 | 0.75
ρth is a constant relating to cable construction
U/UTP |  |  | 5
F/UTP |  |  | 3
U/FTP |  |  | 2.9
F/FTP |  |  | 2.85
XTP |  |  | 2.8
S/FTP |  |  | 2.75
Nb of cond |  | Ic min | Ic max | I |  | PoE app
4 | 0 | 0 | 0.15 | 0 | 0 | PoE
4 | 0 | 0.15 | 0.3 | 0 | 0 | PoE+
8 | 1 | 0 | 0.3 | 0 | 0 | 4p-PoE type 3
8 | 1 | 0.3 | 0.5 | 1 | 1 | 4p-PoE type 4
1
PD input power | 0 | Class | Min Vpse | Max Ppse | Nb of conductors
3.84 | 0 | 1 | 44 | 4 | 4 | 8
6.49 | 0 | 2 | 44 | 7 | 4 | 8
12.95 | 0 | 3 | 44 | 15.4 | 4 | 8
25.5 | 1 | 4 | 50 | 30 | 4 | 8
40 | 0 | 5 | 50 | 45 | 8
51 | 0 | 6 | 50 | 60 | 8
62 | 0 | 7 | 52 | 75 | 8
71.3 | 0 | 8 | 52 | 90 | 8
1000 | 0 | Exceeds class 8 | N/A |  | 0 | 0
|  |  |  | Nb cond list | 4 | 8

## Cable and cord selector (hidden)
Value_1 | Value_2 | Value_3 | CR
Cat.6 | U/UTP | Dca | VDICD116118GHD
List #1 | List #2 | List #3
Cat.5e | U/UTP | Dca
Cat.6 | F/UTP
Cat.6A | U/FTP
Cat.7 | SF/UTP
Cat.7A
Categories | Constructions |  |  | Euroclass 1 | Euroclass 2 | Euroclass 3 | Euroclass 4 | CR
Cat.5e_1 | U/UTP |  | Cat.5e_U/UTP | Dca |  |  |  | 115218
Cat.5e_2 | F/UTP |  | Cat.5e_F/UTP | Dca |  |  |  | 135218
Cat.6_1 | U/UTP |  | Cat.6_U/UTP | Dca |  |  |  | 116118GHD
Cat.6_2 | F/UTP |  | Cat.6_F/UTP | Dca |  |  |  | 136218
Cat.6_3 | U/FTP |  | Cat.6_U/FTP | Dca |  |  |  | 626218
Cat.6_4 | SF/UTP |  | Cat.6_SF/UTP | Dca |  |  |  | 176218
Cat.6A_1 | U/UTP |  | Cat.6A_U/UTP | Dca |  |  |  | 60X218
Cat.6A_2 | F/UTP |  | Cat.6A_F/UTP | Dca | Cca |  |  | 63X218
Cat.6A_3 | U/FTP |  | Cat.6A_U/FTP | Dca |  |  |  | 62X218
Cat.6A_4 | F/FTP |  | Cat.6A_F/FTP | Dca | Cca |  |  | 64X218
Cat.6A_5 | XTP |  | Cat.6A_XTP | Dca | Cca |  |  | 68X218
Cat.7_1 | XTP |  | Cat.7_XTP | Dca |  |  |  | 687218
Cat.7A_1 | F/FTP |  | Cat.7A_F/FTP | Dca | Cca |  |  | 648218
Cat.7A_2 | S/FTP |  | Cat.7A_S/FTP | Dca | Cca |  |  | 658218
Cords @ FD | [5 empty] | Cords @ TO
Copper size | Type | Length | CR |  |  | Copper size | Type | Length | CR
AWG28/7 | Cat.6A STP | 2 | ACTPC6ASFLS20yy (yy = color code) |  |  | AWG28/7 | Cat.6A STP | 2 | ACTPC6ASFLS20yy (yy = color code)
List #1 | List #2 |  |  |  |  | List #1 | List #2
AWG28/7 | Cat.6 UTP |  |  |  |  | AWG28/7 | Cat.6 UTP
AWG26/7 | Cat.6 FTP |  |  |  |  | AWG26/7 | Cat.6 FTP
| Cat.6A STP | [5 empty] | Cat.6A STP
Copper gauge | Categories |  |  | CR (start) | CR (end)
AWG26/7_1 | Cat.5e UTP |  | AWG26/7_Cat.5e UTP | VDIP1815460 | (legacy range)
AWG26/7_2 | Cat.5e FTP |  | AWG26/7_Cat.5e FTP | VDIP1845460 | (legacy range)
AWG26/7_3 | Cat.6 UTP |  | AWG26/7_Cat.6 UTP | VDIP1816460 | (legacy range)
AWG26/7_4 | Cat.6 FTP |  | AWG26/7_Cat.6 FTP | VDIP1846460 | (legacy range)
AWG26/7_5 | Cat.6A UTP |  | AWG26/7_Cat.6A UTP | VDIP181X460 | (legacy range)
AWG26/7_6 | Cat.6A STP |  | AWG26/7_Cat.6A STP | VDIP185X460 | (legacy range)
AWG28/7_1 | Cat.6 UTP |  | AWG28/7_Cat.6 UTP | ACTPC6UULS | yy (yy = color code)
AWG28/7_2 | Cat.6 FTP |  | AWG28/7_Cat.6 FTP | ACTPC6FULS | yy (yy = color code)
AWG28/7_3 | Cat.6A STP |  | AWG28/7_Cat.6A STP | ACTPC6ASFLS | yy (yy = color code)

## Bundle in pathway (hidden)
number of cable | 48
Cable reference | VDICD116118GHD
Cable diameter | 5.5
Pathway width | 100
Pathway height | 50
Reality index | 10% | 6.05
| number of cables (ideal world) |  | number of cables (reality) |  |  | number of cables (reality) | Height
Layer 20
Layer 19 |  |  |  |  | Even layer | 16 | 11.2895
Layer 18 |  |  |  |  | Odd layer | 16 | 6.05
Layer 17
Layer 16 |  |  |  |  | Max nb of layers | 8 | 9.2336
Layer 15 |  |  |  |  | Max nb of cables | 128
Layer 14 |  |  |  |  | Filling ratio | 37.5%
Layer 13 |  |  |  |  | Number of layers | 3 | 16.5289
Layer 12 |  |  |  |  | Rounded up | 3 | 16.5289
Layer 11
Layer 10 |  |  |  |  | Bundle height | 3 | 16.5289
Layer 9 |  |  |  |  | Bundle width |  | 99.825
Layer 8 |  |  |  |  | Bundle w/h ratio |  | 6.0394
Layer 7 | [6 empty] | 0.61882 | L/h ratio | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Layer 6 | [6 empty] | 0.62 | ΔT coefficient | 0.89 | 0.84 | 0.77 | 0.71 | 0.66 | 0.62 | 0.59 | 0.56 | 0.53 | 0.51
Layer 5 | [6 empty] | 0.59
Layer 4 |  | 0 |  | 0
Layer 3 | 13 | 13 | 16 | 16
Layer 2 | 17 | 30 | 16 | 32
Layer 1 | 18 | 48 | 16 | 48
Number of layers |  | 3.7222 |  | 4
Bundle height |  | 18.4663 |  | 21.2184
L/h ratio |  | 5.4153 |  | 4.7129
ΔT coefficient |  | 0.64339 |  | 0.67436
|  | 0.66 |  | 0.71
|  | 0.62 |  | 0.66
Filling rate |  | 36.93% |  | 42.44%

## Messages (hidden)
SETTINGS
Cell
| 0 | 1- Equipment cord settings
c8 | 0 | Selection does not exist, change items a, b and c
c12 | 0 | Bundle size shall be between 1 and 24
c13 | 0 | Ambient temperature shall be between 20 and 60°C
| 0 | 2- Horizontal cable settings
c21 | 0 | Selection does not exist, change items d, e and f
c24 | 0 | Length shall be between 10 and 90 m
c25 | 0 | Bundle size shall be between 1 and 199
c26 | 0 | Ambient temperature shall be between 20 and 60°C
| 0 | 3- Work area cord settings
c32 | 0 | Selection does not exist, change items g, h and i
c36 | 0 | Ambient temperature shall be between 20 and 60°C
| 0 | Horizontal cable pathway
F9 | 0 | Width shall be between 50 and 1000 mm
F10 | 0 | Height shall be between 50 and 200 mm
| 0 | Power over Ethernet
N4 | 0 | Power @ PD shall be smaller than 71.3W
N6 | 0 | Nb of conductors shall be 8
1
2
3
4
5
CABLE INFORMATION
G9 |  | VDICD116118GHD Ø 5,5 mm R = 76,5 Ω/km
WARNING
11 | 1
12 | 2 | temperature increase in bundle is between +10 and +15°C
13 | 3 | temperature increase in bundle exceeds +15°C
21 | 2 | temperature in bundle is between 50 and 60°C
22 | 2 | temperature increase in bundle is between +10 and +15°C
23 | 3 | temperature increase in bundle exceeds +15°C
31 | 3 | temperature in bundle exceeds 60°C
32 | 3 | temperature in bundle exceeds 60°C
33 | 3 | temperature increase in bundle exceeds +15°C
WARNING !
WARNING ROUND BUNDLE
1
1
WARNING FLAT BUNDLE
1
1
WARNING 24-CABLE BUNDLE
1
1

## Calc-round bundle (hidden)
|  | FD cord |  | Cable |  | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord
Reference |  | AWG28/7_Cat.6A STP |  | VDICD116118GHD |  | AWG28/7_Cat.6A STP | Ptot | 0.70795 | 26.6694 | 0.058996 | Ptot | 0.70962 | 26.7254 | 0.059039 | Ptot | 0.70962 | 26.7255 | 0.059039 | Ptot | 0.70962 | 26.7255 | 0.059039
Length |  | 2 |  | 50 |  | 2 | ΔTu (Ptot) | 0.53779 | 0.40519 | 0.15525 | ΔTu (Ptot) | 0.53906 | 0.40604 | 0.15536 | ΔTu (Ptot) | 0.53906 | 0.40604 | 0.15536 | ΔTu (Ptot) | 0.53906 | 0.40604 | 0.15536
Cable factor (ρth) |  | 2.75 |  | 5 |  | 2.75 | ΔTth (Ptot) | 0.077256 | 0.21166 | 0.006438 | ΔTth (Ptot) | 0.077439 | 0.21211 | 0.0064428 | ΔTth (Ptot) | 0.077439 | 0.21211 | 0.0064428 | ΔTth (Ptot) | 0.077439 | 0.21211 | 0.0064428
Cable diameter |  | 5.5 |  | 5.5 |  | 5.5
Environment factor (ρu) |  | 0.15 |  | 0.15 |  | 0.15 |  |  |  |  | Rcable avg | 0.22334 | 2.1029 | 0.22298 | Rcable avg | 0.22335 | 2.1029 | 0.22298 | Rcable avg | 0.22335 | 2.1029 | 0.22298
R(20°C) |  | 0.44568 |  | 3.8245 |  | 0.44568 |  |  |  |  | R | 2.5259 | 0.64633 | 2.5262 | R | 2.5259 | 0.64633 | 2.5262 | R | 2.5259 | 0.64633 | 2.5262
Ambient temperature |  | 20 |  | 45 |  | 20 | [16 empty] | Tmax | Tmax
R(ambient) |  | 0.44568 |  | 4.1974 |  | 0.44568 | [12 empty] | ΔTmax | 0.6 | 0.6 | 0.2 | 1 | 1
Rcable(ambient) |  | 0.22284 |  | 2.0987 |  | 0.22284 | [12 empty] | Tmax | 21 | 46 | 20 | ΔTmax | ΔTmax
Rconnections |  | 0.2 | [16 empty] | Display | 21°C (+0,6°C) | 46°C (+0,6°C) | 20°C (+0,2°C) | 1 | 1
Icable(ambient) |  | 0.51453 | [20 empty] | 11 | 11
IL(°C) coeff < 40°C |  | 0.2 |  | 0.4 |  | 0.2 | [12 empty] | IL ratio | 1.95 | 1 | 1.95
IL(°C) coeff > 40°C |  | 0.2 |  | 0.6 |  | 0.2 | [12 empty] | Equivalent length | 3.9048 | 56.4128 | 3.9013
Number of cables |  | 12 |  | 48 |  | 1 | [12 empty] | Total | 64.2188
Nombre de cables |  | 24 | [16 empty] | Channel IL | 61.75% | Permanent Link IL | 62.68%
Ratio (C16/C15) |  | 1
[19 empty] | Avg power losses | 0.059135 | 0.55678 | 0.059039
FD cord # | x | y | L | 0.5 | 0.28868 |  | Rcable(ambient) | Icable(ambient) | Pcable(ambient) | Tcable | Rcable | Icable | Pcable | Tcable | Rcable | Icable | Pcable | Tcable | Rcable | Icable | Pcable | Tcable
1 | 0 | 0 | 0 | 0 | 0 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51456 | 0.059142 | 0.60869 | 0.22337 | 0.51456 | 0.059142 | 0.60869 | 0.22337 | 0.51456 | 0.059142 | 0.60869
2 | 1 | 0 | 1 | 1 | 0 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51456 | 0.059142 | 0.60869 | 0.22337 | 0.51456 | 0.059142 | 0.60869 | 0.22337 | 0.51456 | 0.059142 | 0.60869
3 | 0.5 | 0.86603 | 1 | 0.5 | 0.86603 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51456 | 0.059142 | 0.60869 | 0.22337 | 0.51456 | 0.059142 | 0.60869 | 0.22337 | 0.51456 | 0.059142 | 0.60869
4 | -0.5 | 0.86603 | 1 | -0.5 | 0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51456 | 0.059136 | 0.58526 | 0.22335 | 0.51456 | 0.059137 | 0.58527 | 0.22335 | 0.51456 | 0.059137 | 0.58527
5 | -1 | 0 | 1 | -1 | 0 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184
6 | -0.5 | -0.86603 | 1 | -0.5 | -0.86603 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184
7 | 0.5 | -0.86603 | 1 | 0.5 | -0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51456 | 0.059136 | 0.58526 | 0.22335 | 0.51456 | 0.059137 | 0.58527 | 0.22335 | 0.51456 | 0.059137 | 0.58527
8 | 1.5 | -0.86603 | 1.7321 | 1.5 | -0.86603 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184
9 | 2 | 0 | 2 | 2 | 0 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184
10 | 1.5 | 0.86603 | 1.7321 | 1.5 | 0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51456 | 0.059136 | 0.58526 | 0.22335 | 0.51456 | 0.059137 | 0.58527 | 0.22335 | 0.51456 | 0.059137 | 0.58527
11 | 1 | 1.7321 | 2 | 1 | 1.7321 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184
12 | 0 | 1.7321 | 1.7321 | 0 | 1.7321 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184 | 0.22333 | 0.51456 | 0.059131 | 0.56184
| -1 | 1.7321 | 2
| -1.5 | 0.86603 | 1.7321
| -2 | 0 | 2
| -1.5 | -0.86603 | 1.7321
| -1 | -1.7321 | 2
| 0 | -1.7321 | 1.7321
| 1 | -1.7321 | 2
| 2 | -1.7321 | 2.6458
| 2.5 | -0.86603 | 2.6458
| 3 | 0 | 3
| 2.5 | 0.86603 | 2.6458
| 2 | 1.7321 | 2.6458
EU Cord | x | y | L
1 | 0 | 0 | 0 | 0 | 0 |  | 0.22284 | 0.51453 | 0.058996 | 0.16168 | 0.22298 | 0.51456 | 0.059039 | 0.1618 | 0.22298 | 0.51456 | 0.059039 | 0.1618 | 0.22298 | 0.51456 | 0.059039 | 0.1618
Cable # | x | y | L | 0.5 | 0.28868
1 | 0 | 0 | 0 | 0 | 0 | 0.57735 | 2.0987 | 0.51453 | 0.55561 | 0.61151 | 2.1037 | 0.51456 | 0.55701 | 0.6128 | 2.1037 | 0.51456 | 0.55701 | 0.6128 | 2.1037 | 0.51456 | 0.55701 | 0.6128
2 | 1 | 0 | 1 | 1 | 0 | 0.57735 | 2.0987 | 0.51453 | 0.55561 | 0.61151 | 2.1037 | 0.51456 | 0.55701 | 0.6128 | 2.1037 | 0.51456 | 0.55701 | 0.6128 | 2.1037 | 0.51456 | 0.55701 | 0.6128
3 | 0.5 | 0.86603 | 1 | 0.5 | 0.86603 | 0.57735 | 2.0987 | 0.51453 | 0.55561 | 0.61151 | 2.1037 | 0.51456 | 0.55701 | 0.6128 | 2.1037 | 0.51456 | 0.55701 | 0.6128 | 2.1037 | 0.51456 | 0.55701 | 0.6128
4 | -0.5 | 0.86603 | 1 | -0.5 | 0.86603 | 1.1547 | 2.0987 | 0.51453 | 0.55561 | 0.5955 | 2.1036 | 0.51456 | 0.55697 | 0.59676 | 2.1036 | 0.51456 | 0.55697 | 0.59676 | 2.1036 | 0.51456 | 0.55697 | 0.59676
5 | -1 | 0 | 1 | -1 | 0 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.5795 | 2.1034 | 0.51456 | 0.55693 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072
6 | -0.5 | -0.86603 | 1 | -0.5 | -0.86603 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.5795 | 2.1034 | 0.51456 | 0.55693 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072
7 | 0.5 | -0.86603 | 1 | 0.5 | -0.86603 | 1.1547 | 2.0987 | 0.51453 | 0.55561 | 0.5955 | 2.1036 | 0.51456 | 0.55697 | 0.59676 | 2.1036 | 0.51456 | 0.55697 | 0.59676 | 2.1036 | 0.51456 | 0.55697 | 0.59676
8 | 1.5 | -0.86603 | 1.7321 | 1.5 | -0.86603 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.5795 | 2.1034 | 0.51456 | 0.55693 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072
9 | 2 | 0 | 2 | 2 | 0 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.5795 | 2.1034 | 0.51456 | 0.55693 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072
10 | 1.5 | 0.86603 | 1.7321 | 1.5 | 0.86603 | 1.1547 | 2.0987 | 0.51453 | 0.55561 | 0.5955 | 2.1036 | 0.51456 | 0.55697 | 0.59676 | 2.1036 | 0.51456 | 0.55697 | 0.59676 | 2.1036 | 0.51456 | 0.55697 | 0.59676
11 | 1 | 1.7321 | 2 | 1 | 1.7321 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.5795 | 2.1034 | 0.51456 | 0.55693 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072
12 | 0 | 1.7321 | 1.7321 | 0 | 1.7321 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.5795 | 2.1034 | 0.51456 | 0.55693 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072 | 2.1034 | 0.51456 | 0.55694 | 0.58072
13 | -1 | 1.7321 | 2 | -1 | 1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.54748 | 2.1032 | 0.51456 | 0.55686 | 0.54863 | 2.1032 | 0.51456 | 0.55686 | 0.54864 | 2.1032 | 0.51456 | 0.55686 | 0.54864
14 | -1.5 | 0.86603 | 1.7321 | -1.5 | 0.86603 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.54748 | 2.1032 | 0.51456 | 0.55686 | 0.54863 | 2.1032 | 0.51456 | 0.55686 | 0.54864 | 2.1032 | 0.51456 | 0.55686 | 0.54864
15 | -2 | 0 | 2 | -2 | 0 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.51547 | 2.1029 | 0.51456 | 0.55679 | 0.51655 | 2.1029 | 0.51456 | 0.55679 | 0.51656 | 2.1029 | 0.51456 | 0.55679 | 0.51656
16 | -1.5 | -0.86603 | 1.7321 | -1.5 | -0.86603 | 2.3094 | 2.0987 | 0.51453 | 0.55561 | 0.53148 | 2.103 | 0.51456 | 0.55682 | 0.53259 | 2.1031 | 0.51456 | 0.55683 | 0.5326 | 2.1031 | 0.51456 | 0.55683 | 0.5326
17 | -1 | -1.7321 | 2 | -1 | -1.7321 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.51547 | 2.1029 | 0.51456 | 0.55679 | 0.51655 | 2.1029 | 0.51456 | 0.55679 | 0.51656 | 2.1029 | 0.51456 | 0.55679 | 0.51656
18 | 0 | -1.7321 | 1.7321 | 0 | -1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.54748 | 2.1032 | 0.51456 | 0.55686 | 0.54863 | 2.1032 | 0.51456 | 0.55686 | 0.54864 | 2.1032 | 0.51456 | 0.55686 | 0.54864
19 | 1 | -1.7321 | 2 | 1 | -1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.54748 | 2.1032 | 0.51456 | 0.55686 | 0.54863 | 2.1032 | 0.51456 | 0.55686 | 0.54864 | 2.1032 | 0.51456 | 0.55686 | 0.54864
20 | 2 | -1.7321 | 2.6458 | 2 | -1.7321 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.51547 | 2.1029 | 0.51456 | 0.55679 | 0.51655 | 2.1029 | 0.51456 | 0.55679 | 0.51656 | 2.1029 | 0.51456 | 0.55679 | 0.51656
21 | 2.5 | -0.86603 | 2.6458 | 2.5 | -0.86603 | 2.3094 | 2.0987 | 0.51453 | 0.55561 | 0.53148 | 2.103 | 0.51456 | 0.55682 | 0.53259 | 2.1031 | 0.51456 | 0.55683 | 0.5326 | 2.1031 | 0.51456 | 0.55683 | 0.5326
22 | 3 | 0 | 3 | 3 | 0 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.51547 | 2.1029 | 0.51456 | 0.55679 | 0.51655 | 2.1029 | 0.51456 | 0.55679 | 0.51656 | 2.1029 | 0.51456 | 0.55679 | 0.51656
23 | 2.5 | 0.86603 | 2.6458 | 2.5 | 0.86603 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.54748 | 2.1032 | 0.51456 | 0.55686 | 0.54863 | 2.1032 | 0.51456 | 0.55686 | 0.54864 | 2.1032 | 0.51456 | 0.55686 | 0.54864
24 | 2 | 1.7321 | 2.6458 | 2 | 1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.54748 | 2.1032 | 0.51456 | 0.55686 | 0.54863 | 2.1032 | 0.51456 | 0.55686 | 0.54864 | 2.1032 | 0.51456 | 0.55686 | 0.54864
25 | 1.5 | 2.5981 | 3 | 1.5 | 2.5981 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.51547 | 2.1029 | 0.51456 | 0.55679 | 0.51655 | 2.1029 | 0.51456 | 0.55679 | 0.51656 | 2.1029 | 0.51456 | 0.55679 | 0.51656
26 | 0.5 | 2.5981 | 2.6458 | 0.5 | 2.5981 | 2.3094 | 2.0987 | 0.51453 | 0.55561 | 0.53148 | 2.103 | 0.51456 | 0.55682 | 0.53259 | 2.1031 | 0.51456 | 0.55683 | 0.5326 | 2.1031 | 0.51456 | 0.55683 | 0.5326
27 | -0.5 | 2.5981 | 2.6458 | -0.5 | 2.5981 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.51547 | 2.1029 | 0.51456 | 0.55679 | 0.51655 | 2.1029 | 0.51456 | 0.55679 | 0.51656 | 2.1029 | 0.51456 | 0.55679 | 0.51656
28 | -1.5 | 2.5981 | 3 | -1.5 | 2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.46745 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843
29 | -2 | 1.7321 | 2.6458 | -2 | 1.7321 | 2.8868 | 2.0987 | 0.51453 | 0.55561 | 0.48346 | 2.1027 | 0.51456 | 0.55672 | 0.48447 | 2.1027 | 0.51456 | 0.55672 | 0.48447 | 2.1027 | 0.51456 | 0.55672 | 0.48447
30 | -2.5 | 0.86603 | 2.6458 | -2.5 | 0.86603 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.46745 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843
31 | -3 | 0 | 3 | -3 | 0 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.41943 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031
32 | -2.5 | -0.86603 | 2.6458 | -2.5 | -0.86603 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.45144 | 2.1024 | 0.51456 | 0.55664 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239
33 | -2 | -1.7321 | 2.6458 | -2 | -1.7321 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.45144 | 2.1024 | 0.51456 | 0.55664 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239
34 | -1.5 | -2.5981 | 3 | -1.5 | -2.5981 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.41943 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031
35 | -0.5 | -2.5981 | 2.6458 | -0.5 | -2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.46745 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843
36 | 0.5 | -2.5981 | 2.6458 | 0.5 | -2.5981 | 2.8868 | 2.0987 | 0.51453 | 0.55561 | 0.48346 | 2.1027 | 0.51456 | 0.55672 | 0.48447 | 2.1027 | 0.51456 | 0.55672 | 0.48447 | 2.1027 | 0.51456 | 0.55672 | 0.48447
37 | 1.5 | -2.5981 | 3 | 1.5 | -2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.46745 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843
38 | 2.5 | -2.5981 | 3.6056 | 2.5 | -2.5981 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.41943 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031
39 | 3 | -1.7321 | 3.4641 | 3 | -1.7321 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.45144 | 2.1024 | 0.51456 | 0.55664 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239
40 | 3.5 | -0.86603 | 3.6056 | 3.5 | -0.86603 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.45144 | 2.1024 | 0.51456 | 0.55664 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239
41 | 4 | 0 | 4 | 4 | 0 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.41943 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031
42 | 3.5 | 0.86603 | 3.6056 | 3.5 | 0.86603 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.46745 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843
43 | 3 | 1.7321 | 3.4641 | 3 | 1.7321 | 2.8868 | 2.0987 | 0.51453 | 0.55561 | 0.48346 | 2.1027 | 0.51456 | 0.55672 | 0.48447 | 2.1027 | 0.51456 | 0.55672 | 0.48447 | 2.1027 | 0.51456 | 0.55672 | 0.48447
44 | 2.5 | 2.5981 | 3.6056 | 2.5 | 2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.46745 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843 | 2.1025 | 0.51456 | 0.55668 | 0.46843
45 | 2 | 3.4641 | 4 | 2 | 3.4641 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.41943 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031
46 | 1 | 3.4641 | 3.6056 | 1 | 3.4641 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.45144 | 2.1024 | 0.51456 | 0.55664 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239
47 | 0 | 3.4641 | 3.4641 | 0 | 3.4641 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.45144 | 2.1024 | 0.51456 | 0.55664 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239 | 2.1024 | 0.51456 | 0.55665 | 0.45239
48 | -1 | 3.4641 | 3.6056 | -1 | 3.4641 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.41943 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031 | 2.1021 | 0.51455 | 0.55657 | 0.42031
| -2 | 3.4641 | 4
| -2.5 | 2.5981 | 3.6056
| -3 | 1.7321 | 3.4641
| -3.5 | 0.86603 | 3.6056
| -4 | 0 | 4
| -3.5 | -0.86603 | 3.6056
| -3 | -1.7321 | 3.4641
| -2.5 | -2.5981 | 3.6056
| -2 | -3.4641 | 4
| -1 | -3.4641 | 3.6056
| 0 | -3.4641 | 3.4641
| 1 | -3.4641 | 3.6056
| 2 | -3.4641 | 4
| 3 | -3.4641 | 4.5826
| 3.5 | -2.5981 | 4.3589
| 4 | -1.7321 | 4.3589
| 4.5 | -0.86603 | 4.5826
| 5 | 0 | 5
| 4.5 | 0.86603 | 4.5826
| 4 | 1.7321 | 4.3589
| 3.5 | 2.5981 | 4.3589
| 3 | 3.4641 | 4.5826
| 2.5 | 4.3301 | 5
| 1.5 | 4.3301 | 4.5826
| 0.5 | 4.3301 | 4.3589
| -0.5 | 4.3301 | 4.3589
| -1.5 | 4.3301 | 4.5826
| -2.5 | 4.3301 | 5
| -3 | 3.4641 | 4.5826
| -3.5 | 2.5981 | 4.3589
| -4 | 1.7321 | 4.3589
| -4.5 | 0.86603 | 4.5826
| -5 | 0 | 5
| -4.5 | -0.86603 | 4.5826
| -4 | -1.7321 | 4.3589
| -3.5 | -2.5981 | 4.3589
| -3 | -3.4641 | 4.5826
| -2.5 | -4.3301 | 5
| -1.5 | -4.3301 | 4.5826
| -0.5 | -4.3301 | 4.3589
| 0.5 | -4.3301 | 4.3589
| 1.5 | -4.3301 | 4.5826
| 2.5 | -4.3301 | 5
| 3.5 | -4.3301 | 5.5678
| 4 | -3.4641 | 5.2915
| 4.5 | -2.5981 | 5.1962
| 5 | -1.7321 | 5.2915
| 5.5 | -0.86603 | 5.5678
| 6 | 0 | 6
| 5.5 | 0.86603 | 5.5678
| 5 | 1.7321 | 5.2915
| 4.5 | 2.5981 | 5.1962
| 4 | 3.4641 | 5.2915
| 3.5 | 4.3301 | 5.5678
| 3 | 5.1962 | 6
| 2 | 5.1962 | 5.5678
| 1 | 5.1962 | 5.2915
| 0 | 5.1962 | 5.1962
| -1 | 5.1962 | 5.2915
| -2 | 5.1962 | 5.5678
| -3 | 5.1962 | 6
| -3.5 | 4.3301 | 5.5678
| -4 | 3.4641 | 5.2915
| -4.5 | 2.5981 | 5.1962
| -5 | 1.7321 | 5.2915
| -5.5 | 0.86603 | 5.5678
| -6 | 0 | 6
| -5.5 | -0.86603 | 5.5678
| -5 | -1.7321 | 5.2915
| -4.5 | -2.5981 | 5.1962
| -4 | -3.4641 | 5.2915
| -3.5 | -4.3301 | 5.5678
| -3 | -5.1962 | 6
| -2 | -5.1962 | 5.5678
| -1 | -5.1962 | 5.2915
| 0 | -5.1962 | 5.1962
| 1 | -5.1962 | 5.2915
| 2 | -5.1962 | 5.5678
| 3 | -5.1962 | 6
| 5.5 | 2.5981 | 6.0828
| 5 | 3.4641 | 6.0828
| 0.5 | 6.0622 | 6.0828
| -0.5 | 6.0622 | 6.0828
| -5 | 3.4641 | 6.0828
| -5.5 | 2.5981 | 6.0828
| -5.5 | -2.5981 | 6.0828
| -5 | -3.4641 | 6.0828
| -0.5 | -6.0622 | 6.0828
| 0.5 | -6.0622 | 6.0828
| 5 | -3.4641 | 6.0828
| 5.5 | -2.5981 | 6.0828
| 6 | 1.7321 | 6.245
| 4.5 | 4.3301 | 6.245
| 1.5 | 6.0622 | 6.245
| -1.5 | 6.0622 | 6.245
| -4.5 | 4.3301 | 6.245
| -6 | 1.7321 | 6.245
| -6 | -1.7321 | 6.245
| -4.5 | -4.3301 | 6.245
| -1.5 | -6.0622 | 6.245
| 1.5 | -6.0622 | 6.245
| 4.5 | -4.3301 | 6.245
| 6 | -1.7321 | 6.245
| 6.5 | 0.86603 | 6.5574
| 4 | 5.1962 | 6.5574
| 2.5 | 6.0622 | 6.5574
| -2.5 | 6.0622 | 6.5574
| -4 | 5.1962 | 6.5574
| -6.5 | 0.86603 | 6.5574
| -6.5 | -0.86603 | 6.5574
| -4 | -5.1962 | 6.5574
| -2.5 | -6.0622 | 6.5574
| 2.5 | -6.0622 | 6.5574
| 4 | -5.1962 | 6.5574
| 6.5 | -0.86603 | 6.5574
| 6 | 3.4641 | 6.9282
| 0 | 6.9282 | 6.9282
| -6 | 3.4641 | 6.9282
| -6 | -3.4641 | 6.9282
| 0 | -6.9282 | 6.9282
| 6 | -3.4641 | 6.9282
| 7 | 0 | 7
| 3.5 | 6.0622 | 7
| -3.5 | 6.0622 | 7
| -7 | 0 | 7
| -3.5 | -6.0622 | 7
| 3.5 | -6.0622 | 7
| 6.5 | 2.5981 | 7
| 5.5 | 4.3301 | 7
| 1 | 6.9282 | 7
| -1 | 6.9282 | 7
| -5.5 | 4.3301 | 7
| -6.5 | 2.5981 | 7
| -6.5 | -2.5981 | 7
| -5.5 | -4.3301 | 7
| -1 | -6.9282 | 7
| 1 | -6.9282 | 7
| 5.5 | -4.3301 | 7
| 6.5 | -2.5981 | 7
| 7 | 1.7321 | 7.2111
| 5 | 5.1962 | 7.2111
| 2 | 6.9282 | 7.2111
| -2 | 6.9282 | 7.2111
| -5 | 5.1962 | 7.2111
| -7 | 1.7321 | 7.2111
| -7 | -1.7321 | 7.2111
| -5 | -5.1962 | 7.2111
| -2 | -6.9282 | 7.2111
| 2 | -6.9282 | 7.2111
| 5 | -5.1962 | 7.2111
| 7 | -1.7321 | 7.2111

## Calc-flat bundle (hidden)
|  | FD cord |  | Cable |  | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord
Reference |  | AWG28/7_Cat.6A STP |  | VDICD116118GHD |  | AWG28/7_Cat.6A STP | Ptot | 0.70795 | 26.6694 | 0.058996 | Ptot | 0.7096 | 26.7042 | 0.059037 | Ptot | 0.7096 | 26.7043 | 0.059037 | Ptot | 0.7096 | 26.7043 | 0.059037
Length |  | 2 |  | 50 |  | 2 | ΔTu (Ptot) | 0.53779 | 0.25074 | 0.15525 | ΔTu (Ptot) | 0.53904 | 0.25106 | 0.15536 | ΔTu (Ptot) | 0.53904 | 0.25106 | 0.15536 | ΔTu (Ptot) | 0.53904 | 0.25106 | 0.15536
Cable factor (ρth) |  | 2.75 |  | 5 |  | 2.75 | ΔTth (Ptot) | 0.077256 | 0.13098 | 0.006438 | ΔTth (Ptot) | 0.077436 | 0.13115 | 0.0064425 | ΔTth (Ptot) | 0.077436 | 0.13115 | 0.0064426 | ΔTth (Ptot) | 0.077436 | 0.13115 | 0.0064426
Cable diameter |  | 5.5 |  | 5.5 |  | 5.5
Environment factor (ρu) |  | 0.15 |  | 0.15 |  | 0.15 |  |  |  |  | Rcable avg | 0.22334 | 2.1013 | 0.22298 | Rcable avg | 0.22335 | 2.1013 | 0.22298 | Rcable avg | 0.22335 | 2.1013 | 0.22298
R(20°C) |  | 0.44568 |  | 3.8245 |  | 0.44568 |  |  |  |  | R | 2.5243 | 0.64633 | 2.5246 | R | 2.5243 | 0.64633 | 2.5246 | R | 2.5243 | 0.64633 | 2.5246
Ambient temperature |  | 20 |  | 45 |  | 20 | [16 empty] | Tmax | Tmax
R(ambient) |  | 0.44568 |  | 4.1974 |  | 0.44568 | [12 empty] | ΔTmax | 0.6 | 0.4 | 0.2 | 1 | 1
Rcable(ambient) |  | 0.22284 |  | 2.0987 |  | 0.22284 | [12 empty] | Tmax | 21 | 45 | 20 | ΔTmax | ΔTmax
Rconnections |  | 0.2 | [16 empty] | Display | 21°C (+0,6°C) | 45°C (+0,4°C) | 20°C (+0,2°C) | 1 | 1
Icable(ambient) |  | 0.51453 | [20 empty] | 11 | 11
IL(°C) coeff < 40°C |  | 0.2 |  | 0.4 |  | 0.2 | [12 empty] | IL ratio | 1.95 | 1 | 1.95
IL(°C) coeff > 40°C |  | 0.2 |  | 0.6 |  | 0.2 | [12 empty] | Equivalent length | 3.9048 | 56.3237 | 3.9013
Number of cables |  | 12 |  | 48 |  | 1 | [12 empty] | Total | 64.1297
ΔT coefficient |  |  |  | 0.61882 | [14 empty] | Channel IL | 61.66% | Permanent Link IL | 62.58%
[19 empty] | Avg power losses | 0.059133 | 0.55634 | 0.059037
FD cord # | x | y | L | 0.5 | 0.28868 |  | Rcable(ambient) | Icable(ambient) | Pcable(ambient) | Tcable | Rcable | Icable | Pcable | Tcable | Rcable | Icable | Pcable | Tcable | Rcable | Icable | Pcable | Tcable
1 | 0 | 0 | 0 | 0 | 0 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867
2 | 1 | 0 | 1 | 1 | 0 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867
3 | 0.5 | 0.86603 | 1 | 0.5 | 0.86603 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867
4 | -0.5 | 0.86603 | 1 | -0.5 | 0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51455 | 0.059134 | 0.58524 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525
5 | -1 | 0 | 1 | -1 | 0 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182
6 | -0.5 | -0.86603 | 1 | -0.5 | -0.86603 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182
7 | 0.5 | -0.86603 | 1 | 0.5 | -0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51455 | 0.059134 | 0.58524 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525
8 | 1.5 | -0.86603 | 1.7321 | 1.5 | -0.86603 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182
9 | 2 | 0 | 2 | 2 | 0 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182
10 | 1.5 | 0.86603 | 1.7321 | 1.5 | 0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51455 | 0.059134 | 0.58524 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525
11 | 1 | 1.7321 | 2 | 1 | 1.7321 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182
12 | 0 | 1.7321 | 1.7321 | 0 | 1.7321 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56182
| -1 | 1.7321 | 2
| -1.5 | 0.86603 | 1.7321
| -2 | 0 | 2
| -1.5 | -0.86603 | 1.7321
| -1 | -1.7321 | 2
| 0 | -1.7321 | 1.7321
| 1 | -1.7321 | 2
| 2 | -1.7321 | 2.6458
| 2.5 | -0.86603 | 2.6458
| 3 | 0 | 3
| 2.5 | 0.86603 | 2.6458
| 2 | 1.7321 | 2.6458
EU Cord | x | y | L
1 | 0 | 0 | 0 | 0 | 0 |  | 0.22284 | 0.51453 | 0.058996 | 0.16168 | 0.22298 | 0.51455 | 0.059037 | 0.1618 | 0.22298 | 0.51455 | 0.059037 | 0.1618 | 0.22298 | 0.51455 | 0.059037 | 0.1618
Cable # | x | y | L | 0.5 | 0.28868
1 | 0 | 0 | 0 | 0 | 0 | 0.57735 | 2.0987 | 0.51453 | 0.55561 | 0.37841 | 2.1018 | 0.51455 | 0.55648 | 0.37891 | 2.1018 | 0.51455 | 0.55648 | 0.37891 | 2.1018 | 0.51455 | 0.55648 | 0.37891
2 | 1 | 0 | 1 | 1 | 0 | 0.57735 | 2.0987 | 0.51453 | 0.55561 | 0.37841 | 2.1018 | 0.51455 | 0.55648 | 0.37891 | 2.1018 | 0.51455 | 0.55648 | 0.37891 | 2.1018 | 0.51455 | 0.55648 | 0.37891
3 | 0.5 | 0.86603 | 1 | 0.5 | 0.86603 | 0.57735 | 2.0987 | 0.51453 | 0.55561 | 0.37841 | 2.1018 | 0.51455 | 0.55648 | 0.37891 | 2.1018 | 0.51455 | 0.55648 | 0.37891 | 2.1018 | 0.51455 | 0.55648 | 0.37891
4 | -0.5 | 0.86603 | 1 | -0.5 | 0.86603 | 1.1547 | 2.0987 | 0.51453 | 0.55561 | 0.36851 | 2.1017 | 0.51455 | 0.55646 | 0.36899 | 2.1017 | 0.51455 | 0.55646 | 0.36899 | 2.1017 | 0.51455 | 0.55646 | 0.36899
5 | -1 | 0 | 1 | -1 | 0 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.3586 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907
6 | -0.5 | -0.86603 | 1 | -0.5 | -0.86603 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.3586 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907
7 | 0.5 | -0.86603 | 1 | 0.5 | -0.86603 | 1.1547 | 2.0987 | 0.51453 | 0.55561 | 0.36851 | 2.1017 | 0.51455 | 0.55646 | 0.36899 | 2.1017 | 0.51455 | 0.55646 | 0.36899 | 2.1017 | 0.51455 | 0.55646 | 0.36899
8 | 1.5 | -0.86603 | 1.7321 | 1.5 | -0.86603 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.3586 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907
9 | 2 | 0 | 2 | 2 | 0 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.3586 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907
10 | 1.5 | 0.86603 | 1.7321 | 1.5 | 0.86603 | 1.1547 | 2.0987 | 0.51453 | 0.55561 | 0.36851 | 2.1017 | 0.51455 | 0.55646 | 0.36899 | 2.1017 | 0.51455 | 0.55646 | 0.36899 | 2.1017 | 0.51455 | 0.55646 | 0.36899
11 | 1 | 1.7321 | 2 | 1 | 1.7321 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.3586 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907
12 | 0 | 1.7321 | 1.7321 | 0 | 1.7321 | 1.5275 | 2.0987 | 0.51453 | 0.55561 | 0.3586 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907 | 2.1016 | 0.51455 | 0.55643 | 0.35907
13 | -1 | 1.7321 | 2 | -1 | 1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.33879 | 2.1015 | 0.51455 | 0.55639 | 0.33923 | 2.1015 | 0.51455 | 0.55639 | 0.33924 | 2.1015 | 0.51455 | 0.55639 | 0.33924
14 | -1.5 | 0.86603 | 1.7321 | -1.5 | 0.86603 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.33879 | 2.1015 | 0.51455 | 0.55639 | 0.33923 | 2.1015 | 0.51455 | 0.55639 | 0.33924 | 2.1015 | 0.51455 | 0.55639 | 0.33924
15 | -2 | 0 | 2 | -2 | 0 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.31898 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194
16 | -1.5 | -0.86603 | 1.7321 | -1.5 | -0.86603 | 2.3094 | 2.0987 | 0.51453 | 0.55561 | 0.32889 | 2.1014 | 0.51455 | 0.55637 | 0.32932 | 2.1014 | 0.51455 | 0.55637 | 0.32932 | 2.1014 | 0.51455 | 0.55637 | 0.32932
17 | -1 | -1.7321 | 2 | -1 | -1.7321 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.31898 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194
18 | 0 | -1.7321 | 1.7321 | 0 | -1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.33879 | 2.1015 | 0.51455 | 0.55639 | 0.33923 | 2.1015 | 0.51455 | 0.55639 | 0.33924 | 2.1015 | 0.51455 | 0.55639 | 0.33924
19 | 1 | -1.7321 | 2 | 1 | -1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.33879 | 2.1015 | 0.51455 | 0.55639 | 0.33923 | 2.1015 | 0.51455 | 0.55639 | 0.33924 | 2.1015 | 0.51455 | 0.55639 | 0.33924
20 | 2 | -1.7321 | 2.6458 | 2 | -1.7321 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.31898 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194
21 | 2.5 | -0.86603 | 2.6458 | 2.5 | -0.86603 | 2.3094 | 2.0987 | 0.51453 | 0.55561 | 0.32889 | 2.1014 | 0.51455 | 0.55637 | 0.32932 | 2.1014 | 0.51455 | 0.55637 | 0.32932 | 2.1014 | 0.51455 | 0.55637 | 0.32932
22 | 3 | 0 | 3 | 3 | 0 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.31898 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194
23 | 2.5 | 0.86603 | 2.6458 | 2.5 | 0.86603 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.33879 | 2.1015 | 0.51455 | 0.55639 | 0.33923 | 2.1015 | 0.51455 | 0.55639 | 0.33924 | 2.1015 | 0.51455 | 0.55639 | 0.33924
24 | 2 | 1.7321 | 2.6458 | 2 | 1.7321 | 2.0817 | 2.0987 | 0.51453 | 0.55561 | 0.33879 | 2.1015 | 0.51455 | 0.55639 | 0.33923 | 2.1015 | 0.51455 | 0.55639 | 0.33924 | 2.1015 | 0.51455 | 0.55639 | 0.33924
25 | 1.5 | 2.5981 | 3 | 1.5 | 2.5981 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.31898 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194
26 | 0.5 | 2.5981 | 2.6458 | 0.5 | 2.5981 | 2.3094 | 2.0987 | 0.51453 | 0.55561 | 0.32889 | 2.1014 | 0.51455 | 0.55637 | 0.32932 | 2.1014 | 0.51455 | 0.55637 | 0.32932 | 2.1014 | 0.51455 | 0.55637 | 0.32932
27 | -0.5 | 2.5981 | 2.6458 | -0.5 | 2.5981 | 2.5166 | 2.0987 | 0.51453 | 0.55561 | 0.31898 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194 | 2.1013 | 0.51455 | 0.55634 | 0.3194
28 | -1.5 | 2.5981 | 3 | -1.5 | 2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.28927 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964
29 | -2 | 1.7321 | 2.6458 | -2 | 1.7321 | 2.8868 | 2.0987 | 0.51453 | 0.55561 | 0.29917 | 2.1011 | 0.51455 | 0.5563 | 0.29956 | 2.1011 | 0.51455 | 0.5563 | 0.29956 | 2.1011 | 0.51455 | 0.5563 | 0.29956
30 | -2.5 | 0.86603 | 2.6458 | -2.5 | 0.86603 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.28927 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964
31 | -3 | 0 | 3 | -3 | 0 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.25955 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989
32 | -2.5 | -0.86603 | 2.6458 | -2.5 | -0.86603 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.27936 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973
33 | -2 | -1.7321 | 2.6458 | -2 | -1.7321 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.27936 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973
34 | -1.5 | -2.5981 | 3 | -1.5 | -2.5981 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.25955 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989
35 | -0.5 | -2.5981 | 2.6458 | -0.5 | -2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.28927 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964
36 | 0.5 | -2.5981 | 2.6458 | 0.5 | -2.5981 | 2.8868 | 2.0987 | 0.51453 | 0.55561 | 0.29917 | 2.1011 | 0.51455 | 0.5563 | 0.29956 | 2.1011 | 0.51455 | 0.5563 | 0.29956 | 2.1011 | 0.51455 | 0.5563 | 0.29956
37 | 1.5 | -2.5981 | 3 | 1.5 | -2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.28927 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964
38 | 2.5 | -2.5981 | 3.6056 | 2.5 | -2.5981 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.25955 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989
39 | 3 | -1.7321 | 3.4641 | 3 | -1.7321 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.27936 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973
40 | 3.5 | -0.86603 | 3.6056 | 3.5 | -0.86603 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.27936 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973
41 | 4 | 0 | 4 | 4 | 0 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.25955 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989
42 | 3.5 | 0.86603 | 3.6056 | 3.5 | 0.86603 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.28927 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964
43 | 3 | 1.7321 | 3.4641 | 3 | 1.7321 | 2.8868 | 2.0987 | 0.51453 | 0.55561 | 0.29917 | 2.1011 | 0.51455 | 0.5563 | 0.29956 | 2.1011 | 0.51455 | 0.5563 | 0.29956 | 2.1011 | 0.51455 | 0.5563 | 0.29956
44 | 2.5 | 2.5981 | 3.6056 | 2.5 | 2.5981 | 3.0551 | 2.0987 | 0.51453 | 0.55561 | 0.28927 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964 | 2.1011 | 0.51455 | 0.55628 | 0.28964
45 | 2 | 3.4641 | 4 | 2 | 3.4641 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.25955 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989
46 | 1 | 3.4641 | 3.6056 | 1 | 3.4641 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.27936 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973
47 | 0 | 3.4641 | 3.4641 | 0 | 3.4641 | 3.2146 | 2.0987 | 0.51453 | 0.55561 | 0.27936 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973 | 2.101 | 0.51455 | 0.55625 | 0.27973
48 | -1 | 3.4641 | 3.6056 | -1 | 3.4641 | 3.5119 | 2.0987 | 0.51453 | 0.55561 | 0.25955 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989 | 2.1008 | 0.51455 | 0.55621 | 0.25989
| -2 | 3.4641 | 4
| -2.5 | 2.5981 | 3.6056
| -3 | 1.7321 | 3.4641
| -3.5 | 0.86603 | 3.6056
| -4 | 0 | 4
| -3.5 | -0.86603 | 3.6056
| -3 | -1.7321 | 3.4641
| -2.5 | -2.5981 | 3.6056
| -2 | -3.4641 | 4
| -1 | -3.4641 | 3.6056
| 0 | -3.4641 | 3.4641
| 1 | -3.4641 | 3.6056
| 2 | -3.4641 | 4
| 3 | -3.4641 | 4.5826
| 3.5 | -2.5981 | 4.3589
| 4 | -1.7321 | 4.3589
| 4.5 | -0.86603 | 4.5826
| 5 | 0 | 5
| 4.5 | 0.86603 | 4.5826
| 4 | 1.7321 | 4.3589
| 3.5 | 2.5981 | 4.3589
| 3 | 3.4641 | 4.5826
| 2.5 | 4.3301 | 5
| 1.5 | 4.3301 | 4.5826
| 0.5 | 4.3301 | 4.3589
| -0.5 | 4.3301 | 4.3589
| -1.5 | 4.3301 | 4.5826
| -2.5 | 4.3301 | 5
| -3 | 3.4641 | 4.5826
| -3.5 | 2.5981 | 4.3589
| -4 | 1.7321 | 4.3589
| -4.5 | 0.86603 | 4.5826
| -5 | 0 | 5
| -4.5 | -0.86603 | 4.5826
| -4 | -1.7321 | 4.3589
| -3.5 | -2.5981 | 4.3589
| -3 | -3.4641 | 4.5826
| -2.5 | -4.3301 | 5
| -1.5 | -4.3301 | 4.5826
| -0.5 | -4.3301 | 4.3589
| 0.5 | -4.3301 | 4.3589
| 1.5 | -4.3301 | 4.5826
| 2.5 | -4.3301 | 5
| 3.5 | -4.3301 | 5.5678
| 4 | -3.4641 | 5.2915
| 4.5 | -2.5981 | 5.1962
| 5 | -1.7321 | 5.2915
| 5.5 | -0.86603 | 5.5678
| 6 | 0 | 6
| 5.5 | 0.86603 | 5.5678
| 5 | 1.7321 | 5.2915
| 4.5 | 2.5981 | 5.1962
| 4 | 3.4641 | 5.2915
| 3.5 | 4.3301 | 5.5678
| 3 | 5.1962 | 6
| 2 | 5.1962 | 5.5678
| 1 | 5.1962 | 5.2915
| 0 | 5.1962 | 5.1962
| -1 | 5.1962 | 5.2915
| -2 | 5.1962 | 5.5678
| -3 | 5.1962 | 6
| -3.5 | 4.3301 | 5.5678
| -4 | 3.4641 | 5.2915
| -4.5 | 2.5981 | 5.1962
| -5 | 1.7321 | 5.2915
| -5.5 | 0.86603 | 5.5678
| -6 | 0 | 6
| -5.5 | -0.86603 | 5.5678
| -5 | -1.7321 | 5.2915
| -4.5 | -2.5981 | 5.1962
| -4 | -3.4641 | 5.2915
| -3.5 | -4.3301 | 5.5678
| -3 | -5.1962 | 6
| -2 | -5.1962 | 5.5678
| -1 | -5.1962 | 5.2915
| 0 | -5.1962 | 5.1962
| 1 | -5.1962 | 5.2915
| 2 | -5.1962 | 5.5678
| 3 | -5.1962 | 6
| 5.5 | 2.5981 | 6.0828
| 5 | 3.4641 | 6.0828
| 0.5 | 6.0622 | 6.0828
| -0.5 | 6.0622 | 6.0828
| -5 | 3.4641 | 6.0828
| -5.5 | 2.5981 | 6.0828
| -5.5 | -2.5981 | 6.0828
| -5 | -3.4641 | 6.0828
| -0.5 | -6.0622 | 6.0828
| 0.5 | -6.0622 | 6.0828
| 5 | -3.4641 | 6.0828
| 5.5 | -2.5981 | 6.0828
| 6 | 1.7321 | 6.245
| 4.5 | 4.3301 | 6.245
| 1.5 | 6.0622 | 6.245
| -1.5 | 6.0622 | 6.245
| -4.5 | 4.3301 | 6.245
| -6 | 1.7321 | 6.245
| -6 | -1.7321 | 6.245
| -4.5 | -4.3301 | 6.245
| -1.5 | -6.0622 | 6.245
| 1.5 | -6.0622 | 6.245
| 4.5 | -4.3301 | 6.245
| 6 | -1.7321 | 6.245
| 6.5 | 0.86603 | 6.5574
| 4 | 5.1962 | 6.5574
| 2.5 | 6.0622 | 6.5574
| -2.5 | 6.0622 | 6.5574
| -4 | 5.1962 | 6.5574
| -6.5 | 0.86603 | 6.5574
| -6.5 | -0.86603 | 6.5574
| -4 | -5.1962 | 6.5574
| -2.5 | -6.0622 | 6.5574
| 2.5 | -6.0622 | 6.5574
| 4 | -5.1962 | 6.5574
| 6.5 | -0.86603 | 6.5574
| 6 | 3.4641 | 6.9282
| 0 | 6.9282 | 6.9282
| -6 | 3.4641 | 6.9282
| -6 | -3.4641 | 6.9282
| 0 | -6.9282 | 6.9282
| 6 | -3.4641 | 6.9282
| 7 | 0 | 7
| 3.5 | 6.0622 | 7
| -3.5 | 6.0622 | 7
| -7 | 0 | 7
| -3.5 | -6.0622 | 7
| 3.5 | -6.0622 | 7
| 6.5 | 2.5981 | 7
| 5.5 | 4.3301 | 7
| 1 | 6.9282 | 7
| -1 | 6.9282 | 7
| -5.5 | 4.3301 | 7
| -6.5 | 2.5981 | 7
| -6.5 | -2.5981 | 7
| -5.5 | -4.3301 | 7
| -1 | -6.9282 | 7
| 1 | -6.9282 | 7
| 5.5 | -4.3301 | 7
| 6.5 | -2.5981 | 7
| 7 | 1.7321 | 7.2111
| 5 | 5.1962 | 7.2111
| 2 | 6.9282 | 7.2111
| -2 | 6.9282 | 7.2111
| -5 | 5.1962 | 7.2111
| -7 | 1.7321 | 7.2111
| -7 | -1.7321 | 7.2111
| -5 | -5.1962 | 7.2111
| -2 | -6.9282 | 7.2111
| 2 | -6.9282 | 7.2111
| 5 | -5.1962 | 7.2111
| 7 | -1.7321 | 7.2111

## Calc-24-cable bundle (hidden)
|  | FD cord |  | Cable |  | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord |  | FD cord | Cable | EU cord
Reference |  | AWG28/7_Cat.6A STP |  | VDICD116118GHD |  | AWG28/7_Cat.6A STP | Ptot | 0.70795 | 13.3347 | 0.058996 | Ptot | 0.7096 | 13.3534 | 0.059037 | Ptot | 0.7096 | 13.3534 | 0.059037 | Ptot | 0.7096 | 13.3534 | 0.059037
Length |  | 2 |  | 50 |  | 2 | ΔTu (Ptot) | 0.53779 | 0.28651 | 0.15525 | ΔTu (Ptot) | 0.53904 | 0.28691 | 0.15536 | ΔTu (Ptot) | 0.53905 | 0.28691 | 0.15536 | ΔTu (Ptot) | 0.53905 | 0.28691 | 0.15536
Cable factor (ρth) |  | 2.75 |  | 5 |  | 2.75 | ΔTth (Ptot) | 0.077256 | 0.10583 | 0.006438 | ΔTth (Ptot) | 0.077436 | 0.10598 | 0.0064426 | ΔTth (Ptot) | 0.077437 | 0.10598 | 0.0064426 | ΔTth (Ptot) | 0.077437 | 0.10598 | 0.0064426
Cable diameter |  | 5.5 |  | 5.5 |  | 5.5
Environment factor (ρu) |  | 0.15 |  | 0.15 |  | 0.15 |  |  |  |  | Rcable avg | 0.22334 | 2.1015 | 0.22298 | Rcable avg | 0.22335 | 2.1015 | 0.22298 | Rcable avg | 0.22335 | 2.1015 | 0.22298
R(20°C) |  | 0.44568 |  | 3.8245 |  | 0.44568 |  |  |  |  | R | 2.5245 | 0.64633 | 2.5248 | R | 2.5245 | 0.64633 | 2.5248 | R | 2.5245 | 0.64633 | 2.5248
Ambient temperature |  | 20 |  | 45 |  | 20 | [16 empty] | Tmax | Tmax
R(ambient) |  | 0.44568 |  | 4.1974 |  | 0.44568 | [12 empty] | ΔTmax | 0.6 | 0.4 | 0.2 | 1 | 1
Rcable(ambient) |  | 0.22284 |  | 2.0987 |  | 0.22284 | [12 empty] | Tmax | 21 | 45 | 20 | ΔTmax | ΔTmax
Rconnections |  | 0.2 | [16 empty] | Display | 21°C (+0,6°C) | 45°C (+0,4°C) | 20°C (+0,2°C) | 1 | 1
Icable(ambient) |  | 0.51453 | [20 empty] | 11 | 11
IL(°C) coeff < 40°C |  | 0.2 |  | 0.4 |  | 0.2 | [12 empty] | IL ratio | 1.95 | 1 | 1.95
IL(°C) coeff > 40°C |  | 0.2 |  | 0.6 |  | 0.2 | [12 empty] | Equivalent length | 3.9048 | 56.3274 | 3.9013
Number of cables |  | 12 |  | 24 |  | 1 | [12 empty] | Total | 64.1335
[19 empty] | Channel IL | 61.67% | Permanent Link IL | 62.59%
[19 empty] | Avg power losses | 0.059134 | 0.55639 | 0.059037
FD cord # | x | y | L | 0.5 | 0.28868 |  | Rcable(ambient) | Icable(ambient) | Pcable(ambient) | Tcable | Rcable | Icable | Pcable | Tcable | Rcable | Icable | Pcable | Tcable | Rcable | Icable | Pcable | Tcable
1 | 0 | 0 | 0 | 0 | 0 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867
2 | 1 | 0 | 1 | 1 | 0 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867
3 | 0.5 | 0.86603 | 1 | 0.5 | 0.86603 | 0.57735 | 0.22284 | 0.51453 | 0.058996 | 0.60726 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867 | 0.22337 | 0.51455 | 0.05914 | 0.60867
4 | -0.5 | 0.86603 | 1 | -0.5 | 0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525
5 | -1 | 0 | 1 | -1 | 0 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56183 | 0.22333 | 0.51455 | 0.059129 | 0.56183
6 | -0.5 | -0.86603 | 1 | -0.5 | -0.86603 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56183 | 0.22333 | 0.51455 | 0.059129 | 0.56183
7 | 0.5 | -0.86603 | 1 | 0.5 | -0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525
8 | 1.5 | -0.86603 | 1.7321 | 1.5 | -0.86603 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56183 | 0.22333 | 0.51455 | 0.059129 | 0.56183
9 | 2 | 0 | 2 | 2 | 0 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56183 | 0.22333 | 0.51455 | 0.059129 | 0.56183
10 | 1.5 | 0.86603 | 1.7321 | 1.5 | 0.86603 | 1.1547 | 0.22284 | 0.51453 | 0.058996 | 0.58389 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525 | 0.22335 | 0.51455 | 0.059135 | 0.58525
11 | 1 | 1.7321 | 2 | 1 | 1.7321 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56183 | 0.22333 | 0.51455 | 0.059129 | 0.56183
12 | 0 | 1.7321 | 1.7321 | 0 | 1.7321 | 1.5275 | 0.22284 | 0.51453 | 0.058996 | 0.56052 | 0.22333 | 0.51455 | 0.059129 | 0.56182 | 0.22333 | 0.51455 | 0.059129 | 0.56183 | 0.22333 | 0.51455 | 0.059129 | 0.56183
| -1 | 1.7321 | 2
| -1.5 | 0.86603 | 1.7321
| -2 | 0 | 2
| -1.5 | -0.86603 | 1.7321
| -1 | -1.7321 | 2
| 0 | -1.7321 | 1.7321
| 1 | -1.7321 | 2
| 2 | -1.7321 | 2.6458
| 2.5 | -0.86603 | 2.6458
| 3 | 0 | 3
| 2.5 | 0.86603 | 2.6458
| 2 | 1.7321 | 2.6458
EU Cord | x | y | L
1 | 0 | 0 | 0 | 0 | 0 |  | 0.22284 | 0.51453 | 0.058996 | 0.16168 | 0.22298 | 0.51455 | 0.059037 | 0.1618 | 0.22298 | 0.51455 | 0.059037 | 0.1618 | 0.22298 | 0.51455 | 0.059037 | 0.1618
Cable # | x | y | L | 0.5 | 0
1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 2.0987 | 0.51453 | 0.55561 | 0.38834 | 2.1019 | 0.51455 | 0.5565 | 0.38888 | 2.1019 | 0.51455 | 0.5565 | 0.38888 | 2.1019 | 0.51455 | 0.5565 | 0.38888
2 | 1 | 0 | 1 | 1 | 0 | 0.5 | 2.0987 | 0.51453 | 0.55561 | 0.38834 | 2.1019 | 0.51455 | 0.5565 | 0.38888 | 2.1019 | 0.51455 | 0.5565 | 0.38888 | 2.1019 | 0.51455 | 0.5565 | 0.38888
3 | 0.5 | 0.86603 | 1 | 0.5 | 0.86603 | 0.86603 | 2.0987 | 0.51453 | 0.55561 | 0.38034 | 2.1018 | 0.51455 | 0.55648 | 0.38087 | 2.1018 | 0.51455 | 0.55648 | 0.38087 | 2.1018 | 0.51455 | 0.55648 | 0.38087
4 | -0.5 | 0.86603 | 1 | -0.5 | 0.86603 | 1.3229 | 2.0987 | 0.51453 | 0.55561 | 0.36433 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484
5 | -1 | 0 | 1 | -1 | 0 | 1.5 | 2.0987 | 0.51453 | 0.55561 | 0.35632 | 2.1016 | 0.51455 | 0.55643 | 0.35682 | 2.1016 | 0.51455 | 0.55643 | 0.35682 | 2.1016 | 0.51455 | 0.55643 | 0.35682
6 | -0.5 | -0.86603 | 1 | -0.5 | -0.86603 | 1.3229 | 2.0987 | 0.51453 | 0.55561 | 0.36433 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484
7 | 0.5 | -0.86603 | 1 | 0.5 | -0.86603 | 0.86603 | 2.0987 | 0.51453 | 0.55561 | 0.38034 | 2.1018 | 0.51455 | 0.55648 | 0.38087 | 2.1018 | 0.51455 | 0.55648 | 0.38087 | 2.1018 | 0.51455 | 0.55648 | 0.38087
8 | 1.5 | -0.86603 | 1.7321 | 1.5 | -0.86603 | 1.3229 | 2.0987 | 0.51453 | 0.55561 | 0.36433 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484
9 | 2 | 0 | 2 | 2 | 0 | 1.5 | 2.0987 | 0.51453 | 0.55561 | 0.35632 | 2.1016 | 0.51455 | 0.55643 | 0.35682 | 2.1016 | 0.51455 | 0.55643 | 0.35682 | 2.1016 | 0.51455 | 0.55643 | 0.35682
10 | 1.5 | 0.86603 | 1.7321 | 1.5 | 0.86603 | 1.3229 | 2.0987 | 0.51453 | 0.55561 | 0.36433 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484 | 2.1017 | 0.51455 | 0.55645 | 0.36484
11 | 1 | 1.7321 | 2 | 1 | 1.7321 | 1.8028 | 2.0987 | 0.51453 | 0.55561 | 0.34032 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079
12 | 0 | 1.7321 | 1.7321 | 0 | 1.7321 | 1.8028 | 2.0987 | 0.51453 | 0.55561 | 0.34032 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079
13 | -1 | 1.7321 | 2 | -1 | 1.7321 | 2.2913 | 2.0987 | 0.51453 | 0.55561 | 0.3083 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874
14 | -1.5 | 0.86603 | 1.7321 | -1.5 | 0.86603 | 2.1794 | 2.0987 | 0.51453 | 0.55561 | 0.31631 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675
15 | -2 | 0 | 2 | -2 | 0 | 2.5 | 2.0987 | 0.51453 | 0.55561 | 0.2923 | 2.1011 | 0.51455 | 0.55628 | 0.29271 | 2.1011 | 0.51455 | 0.55628 | 0.29271 | 2.1011 | 0.51455 | 0.55628 | 0.29271
16 | -1.5 | -0.86603 | 1.7321 | -1.5 | -0.86603 | 2.1794 | 2.0987 | 0.51453 | 0.55561 | 0.31631 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675
17 | -1 | -1.7321 | 2 | -1 | -1.7321 | 2.2913 | 2.0987 | 0.51453 | 0.55561 | 0.3083 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874
18 | 0 | -1.7321 | 1.7321 | 0 | -1.7321 | 1.8028 | 2.0987 | 0.51453 | 0.55561 | 0.34032 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079
19 | 1 | -1.7321 | 2 | 1 | -1.7321 | 1.8028 | 2.0987 | 0.51453 | 0.55561 | 0.34032 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079 | 2.1015 | 0.51455 | 0.55639 | 0.34079
20 | 2 | -1.7321 | 2.6458 | 2 | -1.7321 | 2.2913 | 2.0987 | 0.51453 | 0.55561 | 0.3083 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874
21 | 2.5 | -0.86603 | 2.6458 | 2.5 | -0.86603 | 2.1794 | 2.0987 | 0.51453 | 0.55561 | 0.31631 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675
22 | 3 | 0 | 3 | 3 | 0 | 2.5 | 2.0987 | 0.51453 | 0.55561 | 0.2923 | 2.1011 | 0.51455 | 0.55628 | 0.29271 | 2.1011 | 0.51455 | 0.55628 | 0.29271 | 2.1011 | 0.51455 | 0.55628 | 0.29271
23 | 2.5 | 0.86603 | 2.6458 | 2.5 | 0.86603 | 2.1794 | 2.0987 | 0.51453 | 0.55561 | 0.31631 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675 | 2.1013 | 0.51455 | 0.55634 | 0.31675
24 | 2 | 1.7321 | 2.6458 | 2 | 1.7321 | 2.2913 | 2.0987 | 0.51453 | 0.55561 | 0.3083 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874 | 2.1012 | 0.51455 | 0.55632 | 0.30874

## Temperature in bundle
PoE calculator v. 230721
| CABLING DETAILS |  |  |  |  | 1 | HORIZONTAL CABLE PATHWAY |  |  |  | POWER OVER ETHERNET
❶ | Equipment cord (Floor Distributor side) | [9 empty] | Power Device |  |  | Max power @PD | Nb of conductors
| a- Wire gauge | AWG28/7
| b- Category and construction | Cat.6A STP | [8 empty] | Vpse | 50 | Class 1 (RP1) | 3.84 | 4 or 8
| c- Length | 2 | [8 empty] | Power @ PD | 25 | Class 2 (RP1) | 6.49 | 4 or 8
| Patch cord reference | ACTPC6ASFLS20yy (yy = color code) | [8 empty] | Conductors | 8 | Class 3 (RP1) | 12.95 | 4 or 8
|  |  |  | VDICD116118GHD Ø 5,5 mm R = 76,5 Ω/km | [6 empty] | 4 |  | Class 4 (RP2) | 25.5 | 4 or 8
[13 empty] | Class 5 (RP2) | 40 | 8
| Bundle size (24 max) | 12 | [10 empty] | Class 6 (RP2) | 51 | 8
| Ambient temperature | 20 |  |  |  |  | Width | 100 |  |  |  |  | Class 7 (RP2) | 62 | 8
| Note: bundle of patch cords are supposed to be in ventilated envrionment | [5 empty] | Height | 50 |  |  |  |  | Class 8 (RP3) | 71.3 | 8
❷ | Horizontal cable |  | 1 ROUND BUNDLE |  |  |  | 1 FLAT BUNDLE |  |  |  | 24-CABLE BUNDLES
| d- Category | Cat.6
| e- Construction | U/UTP | Equipment cord max T (ΔT) | 21°C (+0,6°C) |  |  | Equipment cord max T (ΔT) |  | 21°C (+0,6°C) |  | Equipment cord max T (ΔT) |  | 21°C (+0,6°C)
| f- CPR Euroclass | Dca | Horizontal cable max T (ΔT) | 46°C (+0,6°C) |  |  | Horizontal cable max T (ΔT) |  | 45°C (+0,4°C) |  | Horizontal cable max T (ΔT) |  | 45°C (+0,4°C)
| Cable reference | VDICD116118GHD | Worst case channel IL | 61.75% |  |  | Worst case channel IL |  | 61.66% |  | Worst case channel IL |  | 61.67%
|  |  | Worst case Perm. Link IL | 62.68% |  |  | Worst case Perm. Link IL |  | 62.58% |  | Worst case Perm. Link IL |  | 62.59%
| Length | 50
| Number of cables (199 max) | 48 | Power @ PSE | 25.675 |  |  | Power @ PSE |  | 25.6745 |  | Power @ PSE |  | 25.6746
| Ambient temperature | 45 | Average power losses | 0.67496 |  |  | Average power losses |  | 0.67451 |  | Average power losses |  | 0.67456
|  |  | Power efficiency (vs PPSE) | 97.37% | RP3 ü |  | Power efficiency (vs PPSE) |  | 97.37% | RP3 ü | Power efficiency (vs PPSE) |  | 97.37% | RP3 ü
|  |  | Energy losses / 24h | 16.199 |  |  | Energy losses / 24h |  | 16.1882 |  | Energy losses / 24h |  | 16.1895
❸ | Work area cord (End user side) |  | Maximum current per pair | 0.25728 |  |  | Maximum current per pair |  | 0.25728 |  | Maximum current per pair |  | 0.25728
| g- Wire gauge | AWG28/7
| h- Category and construction | Cat.6A STP |  |  |  |  | Cable pathway filling ratio |  | 37.5% |  | 24-cable bundle width (W) |  | 33
| i- Length | 2 |  |  |  |  | Width / height ratio |  | 6.0394 |  | Separation distance (S) |  | 10
| Patch cord reference | ACTPC6ASFLS20yy (yy = color code) |  |  |  |  | Bundle height |  | 3
| Ambient temperature | 20
Note on P4: Schneider Electric: 2 options here: set the Power @ PD (powered device) or the current running on all pairs to 1 Amp
Ventilated
Open metal tray
Closed pathway
With insulation
S
W

## Read me first
LICENSING END USER LICENSE AGREEMENT (the “EULA”) The purpose of this Excel file is to roughly evaluate Schneider Electric cable bundle temperature under PoE load. This Calculation File uses a mathematical model described in ISO/IEC TS 29125 and ISO/IEC 14763-2. Whatever the results this file could lead to, we, Schneider Electric, always recommend to respect and apply rules defined by the relevant standards. LIABILITIES You, as the User, expressly acknowledges and accept that Your use of the Calculation File and the performance, fitness and/or accuracy of the Calculation File for any application, environment or purpose within or for which You shall use the Calculation File, is and shall remain Your sole and full responsibility. To the maximum extent permitted by applicable law, the Calculation File is provided “as it is”, with all faults and without warranty. IN NO EVENT SHALL SCHNEIDER ELECTRIC OR ANYONE ELSE BE LIABLE FOR ANY DAMAGE, LOSS OR EXPENSE. The license granted under this EULA does not cover any modification.

## Feuil1 (hidden)
|  | 1 bundle | 2 bundles | 3 bundles | 3 bundles
| Width | 5.5 D | 10.5 D | 10.5 D | 15.5 D
| Height | 4.33 D | 4.33 D
| Pathway width | 33.275 | 63.525 | 63.525 | 93.775
|  | 20.5 D | 25.5 D | 30.5 D | 35.5 D | 40.5 D
|  | 124.025 | 154.275 | 184.525 | 214.775 | 245.025
Cat.6 U/UTP cable, 30°C ambient temperature
Pathway width | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200
Layers | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Number of cables | 54 | 75 | 96 | 114 | 135 | 153 | 174 | 195
Cable max ΔT | 8.3 | 9.9 | 11.3 | 12.2 | 13.2 | 13.9 | 14.7 | 15.4
Layers | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Number of cables | 36 | 50 | 64 | 76 | 90 | 102 | 116 | 130
Cable max ΔT | 5.9 | 6.8 | 7.5 | 7.9 | 8.5 | 8.9 | 9.3 | 9.6
Cat.6A CL-MX cable, 30°C ambient temperature
Pathway width | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200
Layers | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Number of cables | 52 | 68 | 88 | 104 | 128 | 144 | 164 | 184
Cable max ΔT |  | 6.1 | 7.2 | 8.1 | 8.9 | 9.4 | 10 | 10.6
Layers | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Number of cables | 39 | 51 | 66 | 81 | 96 | 108 | 123 | 138
Cable max ΔT | 4.2 | 4.9 | 5.7 | 6.2 | 6.8 | 7.1 | 7.5 | 7.9
Cat.6 F/UTP cable, 30°C ambient temperature
Pathway width | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200
Layers | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Number of cables | 102: 156; 116: 180; 130: 200
Cable max ΔT | 102: 11.5; 116: 12.3; 130: 12.9
Layers | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Number of cables | 102: 117; 116: 135; 130: 150
Cable max ΔT | 102: 8.6; 116: 9.1; 130: 9.5
Cat.6 U/UTP cable, 30°C ambient temperature, ventilated | 90: Cat.6 U/UTP cable, 30°C ambient temperature, open metal tray
Pathway width | 100 | 150 | 200 |  | Pathway width |  | 100 | 150 | 200
Layers | 5.31 | 4.58 | 4.15 |  | Layers |  | 3.75 | 3.33 | 2.8
Number of cables | 85 | 110 | 135 |  | Number of cables |  | 60 | 80 | 91
Cable max ΔT | 10 | 10 | 10 |  | Cable max ΔT |  | 10 | 10 | 10
Cat.6 F/UTP cable, 30°C ambient temperature, ventilated | 90: Cat.6 F/UTP cable, 30°C ambient temperature, open metal tray
Pathway width | 100 | 150 | 200 |  | Pathway width |  | 100 | 150 | 200
Layers | 9.33 | 7.14 | 6.28 |  | Layers |  | 5.92 | 4.92 | 4.48
Number of cables | 112 | 132 | 157 |  | Number of cables |  | 71 | 91 | 112
Cable max ΔT | 10 | 10 | 10 |  | Cable max ΔT |  | 10 | 10 | 10
Cat.6A U/UTP cable, 30°C ambient temperature, ventilated | 90: Cat.6A U/UTP cable, 30°C ambient temperature, open metal tray
Pathway width | 100 | 150 | 200 |  | Pathway width |  | 100 | 150 | 200
Layers | 11.18 | 8.18 | 7.04 |  | Layers |  | 7.09 | 5.65 | 5.09
Number of cables | 123 | 139 | 162 |  | Number of cables |  | 78 | 96 | 117
Cable max ΔT | 10 | 10 | 10 |  | Cable max ΔT |  | 10 | 10 | 10
Cat.6A XTP cable, 30°C ambient temperature, ventilated | 90: Cat.6A XTP cable, 30°C ambient temperature, open metal tray
Pathway width | 100 | 150 | 200 |  | Pathway width |  | 100 | 150 | 200
Layers | 12.27 | 8.82 | 7.57 |  | Layers |  | 7.64 | 6.06 | 5.43
Number of cables | 135 | 150 | 174 |  | Number of cables |  | 84 | 103 | 125
Cable max ΔT | 10 | 10 | 10 |  | Cable max ΔT |  | 10 | 10 | 10
S
W

## Feuil2 (hidden)
Ambient temperature | 25°C |  |  |  |  | Ambient temperature | 25°C |  |  |  |  | Ambient temperature | 25°C
Remote powering | 1A per pair |  |  |  |  | Remote powering | 1A per pair |  |  |  |  | Remote powering | 1A per pair
Horizontal pathway | Ventilated |  |  |  |  | Horizontal pathway | Open metal tray |  |  |  |  | Horizontal pathway | Closed pathway / with insulation
Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width)
VDICD68X218 | 24 | 3.5 | 3 | 46.6 | 1 x 24 | VDICD68X218 | 24 | 5.3 | 4.7 | 46.6 | 1 x 24 | VDICD68X218 | 23 | 9.9
| 48 | 5.4 | 4.4 | 89 | 2 x 24 |  | 48 | 8.1 | 6.5 | 89 | 2 x 24 | (closed pathway) | 24 | 10.1 | 8.8 | 46.6 | 1 x 24
1-layer 24-bundles | 72 | 7.1 | 6.1 | 89 | (2+1) x 24 | 1-layer 24-bundles | 72 | 10.4 | 8.9 | 89 | (2+1) x 24 |  | 48 | 15 | 12 | 89 | 2 x 24
8+ (ΔT<10) |  |  | 5.2 | 131.3 | 3 x 24 | 7 (ΔT<10) |  |  | 7.6 | 131.3 | 3 x 24 | 10-cable bundle (ΔT<10) | 72 | 19.1 | 16.2 | 89 | (2+1) x 24
| 96 | 8.7 | 6.8 | 131.3 | (3 + 1) x 24 | 8 (ΔT<11) | 96 | 12.6 | 9.8 | 131.3 | (3 + 1) x 24 | 24-cable bundle (ΔT<11) |  |  | 13.7 | 131.3 | 3 x 24
|  |  | 5.9 | 173.6 | 4 x 24 |  |  |  | 8.5 | 173.6 | 4 x 24 |  | 96 | 22.8 | 17.7 | 131.3 | (3 + 1) x 24
2-layer 24-bundles | 120 | 10.2 | 8.4 | 131.3 | (3+2) x 24 | 2-layer 24-bundles | 120 | 14.6 | 12 | 131.3 | (3+2) x 24 |  |  |  | 15.1 | 173.6 | 4 x 24
6 (ΔT<10) |  |  | 6.3 | 216 | 5 x 24 | 4 (ΔT<10) |  |  | 8.9 | 216 | 5 x 24
8 (ΔT<11) | 144 | 11.7 | 8.9 | 173.6 | (4+2) x 24 | 4 (ΔT<11) | 144 | 16.5 | 12.5 | 173.6 | (4+2) x 24 | Cable ref. | Nb of cables | ΔT round
|  |  | 7.6 | 216 | (5+1) x 24 |  |  |  | 10.7 | 216 | (5+1) x 24 | VDICD68X218 | 11 | 9.8
|  |  | 6.7 | 258.4 | 6 x 24 |  |  |  | 9.5 | 258.4 | 6 x 24 | (with insulation) | 13 | 10.7
| 168 | 13.1 | 10.3 | 173.6 | (4+3) x 24 |  | 168 | 18.4 | 14.4 | 173.6 | (4+3) x 24 |  | 24 | 15
|  |  | 9 | 216 | (5+2) x 24 |  |  |  | 12.5 | 216 | (5+2) x 24 | 11-cable bundle (ΔT<10) | 48 | 22.3
|  |  | 7.9 | 258.4 | (6+1) x 24 |  |  |  | 11.1 | 258.4 | (6+1) x 24 | 13-cable bundle (ΔT<11)
|  |  | 7.1 | 300.7 | 7 x 24 |  |  |  | 9.9 | 300.7 | 7 x 24
| 192 | 14.4 | 10.3 | 216 | (5+3) x 24 |  | 192 | 20.1 | 14.3 | 216 | (5+3) x 24
|  |  | 9.2 | 258.4 | (6+2) x 24 |  |  |  | 12.7 | 258.4 | (6+2) x 24
|  |  | 8.3 | 300.7 | (7+1) x 24 |  |  |  | 11.4 | 300.7 | (7+1) x 24
|  |  | 7.4 | 343.1 | 8 x 24 |  |  |  | 10.2 | 343.1 | 8 x 24
Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width)
VDICD63X218 | 24 | 3.8 | 3.3 | 45.4 | 1 x 24 | VDICD63X218 | 24 | 5.8 | 5 | 45.4 | 1 x 24 | VDICD63X218 | 20 | 9.8
| 48 | 5.9 | 4.7 | 86.7 | 2 x 24 |  | 48 | 8.7 | 7 | 86.7 | 2 x 24 | (closed pathway) | 24 | 10.9 | 9.5 | 45.4 | 1 x 24
1-layer 24-bundles | 72 | 7.8 | 6.6 | 86.7 | (2+1) x 24 | 1-layer 24-bundles | 72 | 11.3 | 9.7 | 86.7 | (2+1) x 24 |  | 48 | 16.2 | 12.9 | 86.7 | 2 x 24
8+ (ΔT<10) |  |  | 5.7 | 127.9 | 3 x 24 | 5 (ΔT<10) |  |  | 8.2 | 127.9 | 3 x 24 | 20-cable bundle (ΔT<10) | 72 | 20.7 | 17.5 | 86.7 | (2+1) x 24
| 96 | 9.5 | 7.5 | 127.9 | (3 + 1) x 24 | 7 (ΔT<11) | 96 | 13.7 | 10.7 | 127.9 | (3 + 1) x 24 | 24-cable bundle (ΔT<11) |  |  | 14.9 | 127.9 | 3 x 24
|  |  | 6.3 | 169.2 | 4 x 24 |  |  |  | 9 | 169.2 | 4 x 24
2-layer 24-bundles | 120 | 11.2 | 9.2 | 127.9 | (3+2) x 24 | 2-layer 24-bundles | 120 | 15.9 | 13 | 127.9 | (3+2) x 24
6 (ΔT<10) |  |  | 6.9 | 210.4 | 5 x 24 | 3 (ΔT<10) |  |  | 9.7 | 210.4 | 5 x 24
6 (ΔT<11) | 144 | 12.8 | 9.6 | 169.2 | (4+2) x 24 | 4 (ΔT<11) | 144 | 18 | 13.4 | 169.2 | (4+2) x 24 | Cable ref. | Nb of cables | ΔT round
|  |  | 8.3 | 210.4 | (5+1) x 24 |  |  |  | 11.7 | 210.4 | (5+1) x 24 | VDICD63X218 | 10 | 10
|  |  | 7.4 | 251.7 | 6 x 24 |  |  |  | 10.3 | 251.7 | 6 x 24 | (with insulation) | 12 | 11
| 168 | 14.3 | 11.2 | 169.2 | (4+3) x 24 |  | 168 | 20 | 15.5 | 169.2 | (4+3) x 24 |  | 24 | 16.2
|  |  | 9.8 | 210.4 | (5+2) x 24 |  |  |  | 13.7 | 210.4 | (5+2) x 24 | 10-cable bundle (ΔT<10) | 48 | 24.1
|  |  | 8.7 | 251.7 | (6+1) x 24 |  |  |  | 12 | 251.7 | (6+1) x 24 | 12-cable bundle (ΔT<11)
|  |  | 7.7 | 292.9 | 7 x 24 |  |  |  | 10.7 | 292.9 | 7 x 24
| 192 | 15.8 | 11.3 | 210.4 | (5+3) x 24 |  | 192 | 22 | 15.6 | 210.4 | (5+3) x 24
|  |  | 10 | 251.7 | (6+2) x 24 |  |  |  | 13.8 | 251.7 | (6+2) x 24
|  |  | 9 | 292.9 | (7+1) x 24 |  |  |  | 12.4 | 292.9 | (7+1) x 24
|  |  | 8.1 | 334.2 | 8 x 24 |  |  |  | 11.1 | 334.2 | 8 x 24
Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width)
VDICD136218 | 24 | 4.1 | 3.6 | 43 | 1 x 24 | VDICD136218 | 24 | 6.3 | 5.5 | 43 | 1 x 24 | VDICD136218 | 17 | 9.8
| 48 | 6.3 | 5.1 | 82.1 | 2 x 24 |  | 48 | 9.5 | 7.6 | 82.1 | 2 x 24 | (closed pathway) | 20 | 10.8
1-layer 24-bundles | 72 | 8.4 | 7.1 | 82.1 | (2+1) x 24 | 1-layer 24-bundles | 72 | 12.3 | 10.5 | 82.1 | (2+1) x 24 |  | 24 | 11.9 | 10.4 | 43 | 1 x 24
8+ (ΔT<10) |  |  | 6.1 | 121.1 | 3 x 24 | 4 (ΔT<10) |  |  | 8.9 | 121.1 | 3 x 24 | 17-cable bundle (ΔT<10) | 48 | 17.7 | 14.1 | 82.1 | 2 x 24
| 96 | 10.2 | 8 | 121.1 | (3 + 1) x 24 | 5 (ΔT<11) | 96 | 14.8 | 11.6 | 121.1 | (3 + 1) x 24 | 20-cable bundle (ΔT<11) | 72 | 22.6 | 19.2 | 82.1 | (2+1) x 24
|  |  | 6.8 | 160.2 | 4 x 24 |  |  |  | 9.8 | 160.2 | 4 x 24 |  |  |  | 16.2 | 121.1 | 3 x 24
2-layer 24-bundles | 120 | 12 | 9.8 | 121.1 | (3+2) x 24 | 2-layer 24-bundles | 120 | 17.2 | 14.1 | 121.1 | (3+2) x 24
5 (ΔT<10) |  |  | 7.4 | 199.2 | 5 x 24 | No (ΔT<10) |  |  | 10.5 | 199.2 | 5 x 24
6 (ΔT<11) | 144 | 13.7 | 10.3 | 160.2 | (4+2) x 24 | 3 (ΔT<11) | 144 | 19.5 | 14.5 | 160.2 | (4+2) x 24 | Cable ref. | Nb of cables | ΔT round
|  |  | 8.9 | 199.2 | (5+1) x 24 |  |  |  | 12.6 | 199.2 | (5+1) x 24 | VDICD136218 | 8 | 9.7
|  |  | 7.9 | 238.3 | 6 x 24 |  |  |  | 11.1 | 238.3 | 6 x 24 | (with insulation) | 10 | 11
| 168 | 15.3 | 11.9 | 160.2 | (4+3) x 24 |  | 168 | 21.7 | 16.8 | 160.2 | (4+3) x 24 |  | 12 | 12.1
|  |  | 10.5 | 199.2 | (5+2) x 24 |  |  |  | 14.7 | 199.2 | (5+2) x 24 | 8-cable bundle (ΔT<10) | 24 | 17.8
|  |  | 9.3 | 238.3 | (6+1) x 24 |  |  |  | 13 | 238.3 | (6+1) x 24 | 10-cable bundle (ΔT<11) | 48 | 26.4
|  |  | 8.3 | 277.3 | 7 x 24 |  |  |  | 11.6 | 277.3 | 7 x 24
| 192 | 17 | 12.1 | 199.2 | (5+3) x 24 |  | 192 | 23.8 | 16.9 | 199.2 | (5+3) x 24
|  |  | 10.7 | 238.3 | (6+2) x 24 |  |  |  | 14.9 | 238.3 | (6+2) x 24
|  |  | 9.7 | 277.3 | (7+1) x 24 |  |  |  | 13.4 | 277.3 | (7+1) x 24
|  |  | 8.6 | 316.4 | 8 x 24 |  |  |  | 12 | 316.4 | 8 x 24
Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width) |  | Cable ref. | Nb of cables | ΔT round | ΔT flat | (width)
VDICD116118GHD | 24 | 5.6 | 4.9 | 33.3 | 1 x 24 | VDICD116118GHD | 24 | 8.4 | 7.3 | 33.3 | 1 x 24 | VDICD116118GHD | 10 | 9.5
| 48 | 8.8 | 7.1 | 63.6 | 2 x 24 |  | 48 | 12.9 | 10.4 | 63.6 | 2 x 24 | (closed pathway) | 12 | 10.6
1-layer 24-bundles | 72 | 11.8 | 10.1 | 63.6 | (2+1) x 24 | 1-layer 24-bundles | 72 | 16.9 | 14.4 | 63.6 | (2+1) x 24 |  | 24 | 15.7 | 13.7 | 33.3 | 1 x 24
4 (ΔT<10) |  |  | 8.6 | 93.8 | 3 x 24 | 1 (ΔT<10) |  |  | 12.2 | 93.8 | 3 x 24 | 10-cable bundle (ΔT<10) | 48 | 23.7 | 18.9 | 63.6 | 2 x 24
5 (ΔT<11) | 96 | 14.6 | 11.4 | 93.8 | (3 + 1) x 24 | 2 (ΔT<11) | 96 | 20.6 | 16.1 | 93.8 | (3 + 1) x 24 | 12-cable bundle (ΔT<11) | 72 | 30.7 | 25.9 | 63.6 | (2+1) x 24
|  |  | 9.7 | 124.1 | 4 x 24 |  |  |  | 13.6 | 124.1 | 4 x 24 |  |  |  | 21.8 | 93.8 | 3 x 24
2-layer 24-bundles | 120 | 17.3 | 14.1 | 93.8 | (3+2) x 24 | 2-layer 24-bundles | 120 | 24.2 | 19.7 | 93.8 | (3+2) x 24
No (ΔT<10) |  |  | 10.5 | 154.3 | 5 x 24 | No (ΔT<10) |  |  | 14.6 | 154.3 | 5 x 24
3 (ΔT<11) | 144 | 19.9 | 14.8 | 124.1 | (4+2) x 24 | No (ΔT<11) | 144 | 27.6 | 20.4 | 124.1 | (4+2) x 24 | Cable ref. | Nb of cables | ΔT round
|  |  | 12.9 | 154.3 | (5+1) x 24 |  |  |  | 17.7 | 154.3 | (5+1) x 24 | VDICD116118GHD | 5 | 9.8
|  |  | 11.4 | 184.6 | 6 x 24 |  |  |  | 15.6 | 184.6 | 6 x 24 | (with insulation) | 6 | 10.9
| 168 | 22.4 | 17.4 | 124.1 | (4+3) x 24 |  | 168 | 30.9 | 23.8 | 124.1 | (4+3) x 24 |  | 12 | 15.8
|  |  | 15.3 | 154.3 | (5+2) x 24 |  |  |  | 20.9 | 154.3 | (5+2) x 24 | 5-cable bundle (ΔT<10) | 24 | 23.4
|  |  | 13.5 | 184.6 | (6+1) x 24 |  |  |  | 18.3 | 184.6 | (6+1) x 24 | 6-cable bundle (ΔT<11) | 48 | 35.5
|  |  | 12 | 214.8 | 7 x 24 |  |  |  | 16.3 | 214.8 | 7 x 24
| 192 | 24.9 | 17.7 | 154.3 | (5+3) x 24 |  | 192 | 34.1 | 24 | 154.3 | (5+3) x 24
|  |  | 15.7 | 184.6 | (6+2) x 24 |  |  |  | 21.2 | 184.6 | (6+2) x 24
|  |  | 14.1 | 214.8 | (7+1) x 24 |  |  |  | 19 | 214.8 | (7+1) x 24
|  |  | 12.6 | 245.1 | 8 x 24 |  |  |  | 16.9 | 245.1 | 8 x 24

## Feuil4 (hidden)
Cable ref. | R | D | 6 | 12 | 24 | 48 | 72 | 96 | 144 | 216
| 95 | 5 | 3.146 | 4.7163 | 7.2041 | 11.2566 | 14.7905 | 18.0561 | 24.1224 | 32.5562
VDICD115218 | 86.5504 | 4.9 | 2.9162 | 4.3675 | 6.6633 | 10.3968 | 13.6483 | 16.6502 | 22.2219 | 29.9606
(Schneider Electric model) |  |  | 2.9 | 4.4 | 6.7 | 10.7 | 14.2 | 17.5 | 23.7
| 75 | 7 | 1.8769 | 2.8653 | 4.4739 | 7.1705 | 9.5748 | 11.8277 | 16.0714 | 22.0616
VDICD116118GHD | 76.49 | 5.5 | 2.3361 | 3.5189 | 5.4066 | 8.5064 | 11.2266 | 13.7504 | 18.4577 | 25.0314
(Schneider Electric model) |  |  | 2.4 | 3.5 | 5.4 | 8.7 | 11.6 | 14.3 | 19.5
VDICD626218 | 76.0806 | 6.9 | 1.9263 | 2.9381 | 4.5829 | 7.3369 | 9.79 | 12.0874 | 16.4122 | 22.5133
(Schneider Electric model) |  |  | 1.8 | 2.6 | 4 | 6.2 | 8.1 | 9.9 | 13.2
| 65 | 7.7 | 1.5072 | 2.3142 | 3.6383 | 5.8764 | 7.8842 | 9.7726 | 13.3431 | 18.403
VDICD658218 | 69.1548 | 7.6 | 1.6202 | 2.4858 | 3.9043 | 6.2994 | 8.4461 | 10.4642 | 14.2779 | 19.6797
(Schneider Electric model)
Cable ref. | R | D | 6 | 12 | 24 | 48 | 72 | 96 | 144 | 216
| 95 | 5 | 4.0489 | 5.9931 | 9.0098 | 13.8103 | 17.9182 | 21.6676 | 28.5456 | 37.9735
VDICD115218 | 86.5504 | 4.9 | 3.7556 | 5.5546 | 8.3421 | 12.7709 | 16.5559 | 20.0077 | 26.3339 | 34.9968
(Schneider Electric model) | [7 empty] | 25.2
| 75 | 7 | 2.3861 | 3.5853 | 5.4922 | 8.6106 | 11.3385 | 13.8643 | 18.5657 | 25.1165
VDICD116118GHD | 76.49 | 5.5 | 2.997 | 4.4535 | 6.7284 | 10.3756 | 13.516 | 16.3939 | 21.6953 | 28.9967
(Schneider Electric model) | [7 empty] | 20.2
VDICD626218 | 76.0806 | 6.9 | 2.4502 | 3.6791 | 5.6309 | 8.8189 | 11.6051 | 14.1832 | 18.9791 | 25.6571
(Schneider Electric model) | [7 empty] | 14.5
| 65 | 7.7 | 1.9083 | 2.8815 | 4.4406 | 7.011 | 9.2738 | 11.3772 | 15.3083 | 20.8098
VDICD658218 | 69.1548 | 7.6 | 2.0526 | 3.0973 | 4.7691 | 7.5224 | 9.944 | 12.1938 | 16.3962 | 22.2741
(Schneider Electric model)

## Feuil3 (hidden)
|  | Ventilated |  | Open metal tray |  | Closed pathway | With insulation
Cable references | Maximum length 2-pt Perm. Link | 1-layer 24-bundles | 2-layer 24-bundles | 1-layer 24-bundles | 2-layer 24-bundles | Bundle size | Bundle size
VDICD68X218 | 85 | 8 x 24 | 8 x 24 | 8 x 24 | 4 x 24 | 28 | 13
VDICD63X218 | 85 | 8 x 24 | 6 x 24 | 7 x 24 | 4 x 24 | 24 | 12
VDICD136218 | 85 | 8 x 24 | 6 x 24 | 5 x 24 | 3 x 24 | 20 | 10
VDICD116118GHD | 82 | 5 x 24 | 3 x 24 | 2 x 24 | - | 12 | 6